## Sheet1
Eco-$mart, Inc.
4411 Bee Ridge Rd. #344
Sarasota, FL 34233
888-329-2705
Building Energy Efficiency Cost / Benefit Analysis
Lighting Retrofit
Job Name: Example
Melded kWH Rate: |  |  | 0.12
$$ Saved In Air Conditioned / Refrigerated Spaces = Electric Savings * 1.5 (Electricity + A/C + Maintenance Savings)
$$ Saved in Unconditioned Spaces = Electric Savings * 1.2 (Electricity + Maintenance Savings)
Area: Replace 400W MH High Bay / 250W MH Wall Pack Fixtures with 200W Induction High Bay / 100W Induction Wall Pack Fixtures
Retrofit Costs and Savings:
Current | Fixt. | Total | Hrs. | Std. | Proposed | Fixt. | New | Hrs. | New | kW | kWH | Ann. $$ | Retro | Payback
kW/fixt. | Qty. | kW | Used | kWH | kW/fixt. | Qty. | kW | Used | kWH | Saved | Saved | Saved | Cost | (yrs.)
0.45 | 66 | 29.7 | 4380 | 130086 | 0.2 | 66 | 13.2 | 4380 | 57816 | 16.5 | 72270 | 10406.88 | 36300 | 3.4881
0.27 | 19 | 5.13 | 4380 | 22469.4 | 0.1 | 19 | 1.9 | 4380 | 8322 | 3.23 | 14147.4 | 2546.532 | 10450 | 4.1036
[11 empty] | Combined Cost / Payback Period: | 12953.412 | 46750 | 3.6091
Notes | The above analysis represents the costs and savings associated with replacing existing metal halide
warehouse lighting with induction lighting, in the high ceiling storage and refrigeration areas. There are sixty-six
400W MH fixtures (using 450W per fixture). These fixtures can be replaced with induction lights using
200W each. There are nineteen 250W MH wall pack fixtures in the coolers. These fixturescan be replaced with
100W induction lights. Induction lamps are rated at 100,000 hours, versus the 20,000 hours (or 15,000 hours)
ratings for the metal halide lighting. Induction lighting is much higher color rendering than metal halide
(90 CRI versus 65 CRI) meaning the same quantity of light will provide more usable light to the human eye,
creating better visibility. In addition, metal halide lamps typically lose fifty percent of their light output the first
year of operation, where the induction lamps will maintain seventy percent of their light output after ten years.
Cost estimate is based on the wholesale fixture price for the eighty-five fixtures (approximately $450.00 each),
plus $100.00 per fixture for labor.
Please let us know how we can be of service.
Call 888-329-2705 for more information, or visit us on the web at www.eco-smart.com