## Sheet1
Eco-$mart, Inc.
4411 Bee Ridge Rd. #344
Sarasota, FL 34233
888-329-2705
Building Energy Efficiency Cost / Benefit Analysis
Lighting Retrofit
Job Name: Example
Melded kWH Rate: |  |  | 0.12
$$ Saved In Air Conditioned / Refrigerated Spaces = Electric Savings * 1.5 (Electricity + A/C + Maintenance Savings)
$$ Saved in Unconditioned Spaces = Electric Savings * 1.2 (Electricity + Maintenance Savings)
Area: Replace 400W MH High Bay with 200W Induction High Bay (unconditioned space)
Retrofit Costs and Savings:
Current | Fixt. | Total | Hrs. | Std. | Proposed | Fixt. | New | Hrs. | New | kW | kWH | Ann. $$ | Retro | Payback
kW/fixt. | Qty. | kW | Used | kWH | kW/fixt. | Qty. | kW | Used | kWH | Saved | Saved | Saved | Cost | (yrs.)
0.45 | 100 | 45 | 4380 | 197100 | 0.21 | 100 | 21 | 4380 | 91980 | 24 | 105120 | 15137.28 | 50000 | 3.3031
Notes | The above analysis represents the costs and savings associated with replacing existing metal halide
plant floor lighting with induction lighting. 400W MH fixtures (using 450W per fixture)c an be replaced with
induction lights using 210W each.
Induction lamps are rated at 100,000 hours, versus the 20,000 hours (or 15,000 hours)
ratings for the metal halide lighting. Induction lighting is much higher color rendering than metal halide
(90 CRI versus 65 CRI) meaning the same quantity of light will provide more usable light to the human eye,
creating better visibility. In addition, metal halide lamps typically lose fifty percent of their light output the first
year of operation, where the induction lamps will maintain seventy percent of their light output after ten years.
Cost estimate is based on an installed fixture price for the of approximately $500.00 each.
Please let us know how we can be of service.
Call 888-329-2705 for more information, or visit us on the web at www.eco-smart.com