## Instructions
The Lighting Equipment Survey form for Retrofit projects is provided to facilitate the completion of Final Applications that involve lighting measures. Each line item in the survey is generally used to record the lighting fixtures and controls in a single room/area. However, if multiple usage groups1 or fixture types are present in a single room/area, multiple line items should be used to represent each different usage group or fixture type. Information must be supplied for pre-installation and post-installation lighting equipment.
Once the form is complete, Project Sponsor’s are able to upload this equipment survey data directly to the online database. The Initial Application will not require equipment inventory spreadsheets to be uploaded to the system. The Project Sponsor will simply estimate and manually input the kW and kWh savings into the database. However, the following stages in the online process such as the Final Application, Installation Report and Savings Report will require spreadsheets to be uploaded. Each line item consists of three sections:
General Guidelines:
Yellow columns and headings, type in appropriate information.
Orange columns and headings, choose from the drop-down list.
Gray shaded cells are automatically calculated, no user input required.
Section 1 Space Description
Space Description is for the room locations, usage group and coincidence factor information. All cells in this section are to be completed by the Project Sponsor. Additional information regarding the coincidence factor can be found in the M&V Guidelines section of the Program Manual.
Section 2 Pre-retrofit and Post-retrofit Equipment
The Pre-Retrofit Equipment and Post-Retrofit Equipment sections are for specific information about the lighting fixtures. All non-shaded cells require input from the Project Sponsor. The shaded cells, kW per Fixture and kW per Space, are calculated cells and do not require input from the Project Sponsor.
Section 3 Annual kW and Annual kWh Savings
Annual kW Savings and Annual kWh Savings are equations, and do not require input from the Project Sponsor. These equations show only demand and energy savings associated with the lighting retrofit. Any HVAC interactive savings are included in the calculated savings if the facility is defined as conditioned area.
Notes:
1 Usage Groups - When performing the pre-installation activities Project Sponsors should organize the equipment into usage groups. These are collections of equipment (e.g., rooms with lighting fixtures) with similar operating schedules and functional uses. For instance, although a site's open office lighting may have the same annual hours of operation as the private office lighting, the two have different functional uses. In this case, a change in the operating hours of the private office lights due to the installation of an occupancy sensor would not be relevant to the operating hours of the open office lights.

## FA.6
C&I Standard Offer Program: Retrofit Lighting Equipment Inventory Form
Retrofit Lighting Survey Form v1.6 2008
1
Project Name:
Project Site Address:
Sponsor Name:
Please fill out one copy of this form for each customer site involved in the project where lighting measures are being installed.
Fill in all non-shaded cells of the lighting equipment survey. Shaded values are automatically calculated or taken from the Wattage Table. Use drop-down list if available in the cell. To print this form click on File/Print/OK.
[29 empty] | Total Peak kW Savings | Total kWh Savings
Instructions: |  | Yellow columns and headings, type in appropriate information. | [26 empty] | 0 | 0
Orange columns and headings, choose from the drop-down list.
Gray shaded cells are automatically calculated, no user input required.
| Space Description | [6 empty] | Pre-Retrofit Equipment |  |  |  | Post-Retrofit Equipment |  |  |  | Pre-Retrofit Equipment | [6 empty] | Post-Retrofit Equipment |  |  | Annual kW Savings | Annual kWh Savings | Annual kW Savings (includes Interactive Effects) | Total Annual kW Savings (includes Interactive Effects & Coincidence Factor) | Total Annual kWh Savings (includes Interactive Effects)
Line Item | Building | Floor | Area Description | Room Description | Building Type (select from drop-down list) | Air Conditioning Type (select from drop-down list) | Fixture Code | # of Fixtures | # of Non-op Fixtures* | Pre Control Device Description (select from drop-down list) | Fixture Code | # of Fixtures | Post Control Device Description (select from drop-down list) | Coincidence Factor | % Non-operative Fixtures * | kW per Fixture * | kW per Space | kWh per Space | Power Adjustment Factor | Pre Operating Hours | kW per Fixture | kW per Space | kWh per Space | Power Adjustment Factor | Post Operating Hours
1 | [13 empty] | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
2 | [13 empty] | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
3 | [13 empty] | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
4 | [13 empty] | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
5 | [13 empty] | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
6 | [13 empty] | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
7 | [13 empty] | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
8 | [13 empty] | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
9 | [13 empty] | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
10 | [13 empty] | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
11 | [13 empty] | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
12 | [13 empty] | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
13 | [13 empty] | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
14 | [13 empty] | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
15 | [13 empty] | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
16 | [13 empty] | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
17 | [13 empty] | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
18 | [13 empty] | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
19 | [13 empty] | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
20 | [13 empty] | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
21 | [13 empty] | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
22 | [13 empty] | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
23 | [13 empty] | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
24 | [13 empty] | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
25 | [13 empty] | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
26 | [13 empty] | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
27 | [13 empty] | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
28 | [13 empty] | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
29 | [13 empty] | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
30 | [13 empty] | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
31 | [13 empty] | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
32 | [13 empty] | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
33 | [13 empty] | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
34 | [13 empty] | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
35 | [13 empty] | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
36 | [13 empty] | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
37 | [13 empty] | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
38 | [13 empty] | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
39 | [13 empty] | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
40 | [13 empty] | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
41 | [13 empty] | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
42 | [13 empty] | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
43 | [13 empty] | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
44 | [13 empty] | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
45 | [13 empty] | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
46 | [13 empty] | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
47 | [13 empty] | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
48 | [13 empty] | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
49 | [13 empty] | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
50 | [13 empty] | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
51 | [13 empty] | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
52 | [13 empty] | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
53 | [13 empty] | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
54 | [13 empty] | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
55 | [13 empty] | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
56 | [13 empty] | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
57 | [13 empty] | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
58 | [13 empty] | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
59 | [13 empty] | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
60 | [13 empty] | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
61 | [13 empty] | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
62 | [13 empty] | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
63 | [13 empty] | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
64 | [13 empty] | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
65 | [13 empty] | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
66 | [13 empty] | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
67 | [13 empty] | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
68 | [13 empty] | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
69 | [13 empty] | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
70 | [13 empty] | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
71 | [13 empty] | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
72 | [13 empty] | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
73 | [13 empty] | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
74 | [13 empty] | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
75 | [13 empty] | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
76 | [13 empty] | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
77 | [13 empty] | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
78 | [13 empty] | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
79 | [13 empty] | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
80 | [13 empty] | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
81 | [13 empty] | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
82 | [13 empty] | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
83 | [13 empty] | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
84 | [13 empty] | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
85 | [13 empty] | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
86 | [13 empty] | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
87 | [13 empty] | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
88 | [13 empty] | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
89 | [13 empty] | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
90 | [13 empty] | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
91 | [13 empty] | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
92 | [13 empty] | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
93 | [13 empty] | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
94 | [13 empty] | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
95 | [13 empty] | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
96 | [13 empty] | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
97 | [13 empty] | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
98 | [13 empty] | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
99 | [13 empty] | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
100 | [13 empty] | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
101 | [13 empty] | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
102 | [13 empty] | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
103 | [13 empty] | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
104 | [13 empty] | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
105 | [13 empty] | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
106 | [13 empty] | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
107 | [13 empty] | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
108 | [13 empty] | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
109 | [13 empty] | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
110 | [13 empty] | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
111 | [13 empty] | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
112 | [13 empty] | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
113 | [13 empty] | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
114 | [13 empty] | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
115 | [13 empty] | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
116 | [13 empty] | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
117 | [13 empty] | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
118 | [13 empty] | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
119 | [13 empty] | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
120 | [13 empty] | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
121 | [13 empty] | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
122 | [13 empty] | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
123 | [13 empty] | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
124 | [13 empty] | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
125 | [13 empty] | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
126 | [13 empty] | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
127 | [13 empty] | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
128 | [13 empty] | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
129 | [13 empty] | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
130 | [13 empty] | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
131 | [13 empty] | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
132 | [13 empty] | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
133 | [13 empty] | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
134 | [13 empty] | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
135 | [13 empty] | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
136 | [13 empty] | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
137 | [13 empty] | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
138 | [13 empty] | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
139 | [13 empty] | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
140 | [13 empty] | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
141 | [13 empty] | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
142 | [13 empty] | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
143 | [13 empty] | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
144 | [13 empty] | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
145 | [13 empty] | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
146 | [13 empty] | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
147 | [13 empty] | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
148 | [13 empty] | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
149 | [13 empty] | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
150 | [13 empty] | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
151 | [13 empty] | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
152 | [13 empty] | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
153 | [13 empty] | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
154 | [13 empty] | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
155 | [13 empty] | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
156 | [13 empty] | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
157 | [13 empty] | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
158 | [13 empty] | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
159 | [13 empty] | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
160 | [13 empty] | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
161 | [13 empty] | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
162 | [13 empty] | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
163 | [13 empty] | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
164 | [13 empty] | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
165 | [13 empty] | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
166 | [13 empty] | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
167 | [13 empty] | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
168 | [13 empty] | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
169 | [13 empty] | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
170 | [13 empty] | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
171 | [13 empty] | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
172 | [13 empty] | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
173 | [13 empty] | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
174 | [13 empty] | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
175 | [13 empty] | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
176 | [13 empty] | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
177 | [13 empty] | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
178 | [13 empty] | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
179 | [13 empty] | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
180 | [13 empty] | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
181 | [13 empty] | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
182 | [13 empty] | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
183 | [13 empty] | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
184 | [13 empty] | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
185 | [13 empty] | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
186 | [13 empty] | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
187 | [13 empty] | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
188 | [13 empty] | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
189 | [13 empty] | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
190 | [13 empty] | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
191 | [13 empty] | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
192 | [13 empty] | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
193 | [13 empty] | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
194 | [13 empty] | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
195 | [13 empty] | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
196 | [13 empty] | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
197 | [13 empty] | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
198 | [13 empty] | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
199 | [13 empty] | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
200 | [13 empty] | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
201 | [13 empty] | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
202 | [13 empty] | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
203 | [13 empty] | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
204 | [13 empty] | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
205 | [13 empty] | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
206 | [13 empty] | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
207 | [13 empty] | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
208 | [13 empty] | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
209 | [13 empty] | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
210 | [13 empty] | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
211 | [13 empty] | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
212 | [13 empty] | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
213 | [13 empty] | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
214 | [13 empty] | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
215 | [13 empty] | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
216 | [13 empty] | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
217 | [13 empty] | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
218 | [13 empty] | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
219 | [13 empty] | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
220 | [13 empty] | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
221 | [13 empty] | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
222 | [13 empty] | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
223 | [13 empty] | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
224 | [13 empty] | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
225 | [13 empty] | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
226 | [13 empty] | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
227 | [13 empty] | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
228 | [13 empty] | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
229 | [13 empty] | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
230 | [13 empty] | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
231 | [13 empty] | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
232 | [13 empty] | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
233 | [13 empty] | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
234 | [13 empty] | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
235 | [13 empty] | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
236 | [13 empty] | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
237 | [13 empty] | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
238 | [13 empty] | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
239 | [13 empty] | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
240 | [13 empty] | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
241 | [13 empty] | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
242 | [13 empty] | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
243 | [13 empty] | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
244 | [13 empty] | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
245 | [13 empty] | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
246 | [13 empty] | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
247 | [13 empty] | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
248 | [13 empty] | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
249 | [13 empty] | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
250 | [13 empty] | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
If you need more than 250 rows, please contact program administrator.
|  |  |  | % In-operative fixtures: |  |  |  | 0 | 0 |  | Total # Fixtures | 0 |  |  |  |  | 0 | 0 |  |  |  | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
* If the number of non-operating fixtures is greater than 10%, the savings calculation shall be reduced accordingly. | [6 empty] | Pre- kW | Pre- kWh | % NO | % Over 10% | Post- kW | Post- kWh |  |  |  |  | Pre- kW | Pre- kWh |  |  |  | Post- kW | Post- kWh | [5 empty] | Total Peak kW Savings | Total kWh Savings
[7 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | [9 empty] | 0 | 0 |  |  | 0 | 0

## Factor Tables
Operating Hours and Coincidence Factor Table
(for use with Stipulated Hours Method or when coincidence factor will not be measured)
Building Type | Building Type Code | Hours | Coincidence Factor
Stipulated Office | Office | 3760 | 0.8
Stipulated Non-24-Hour Supermarket/Retail/Restaurant | Non-24 hr Retail | 4250 | 0.95
Stipulated Education (K-12; no summer session) | Educ K-12 | 2150 | 0.82
Stipulated 24-Hour Supermarket/Retail | 24 hr Retail | 6900 | 0.95
Stipulated In-Patient Health Care | In-Patient | 3750 | 0.6
Higher Education (College / University) | College | 2085 | 0.67
Multi-Family Housing, Common Areas | MF Common | 4772 | 0.87
Parking Structure | Parking | 7884 | 1
Power Adjustment Factors Table
(**for use with Stipulated Controls Savings Method)
Control Type (DC = Daylight Controls) | PAF Control Code | Power Adjustment Factor (PAF)
No controls measures | None | 1
Stipulated DC - continuous dimming | DC-cont | 0.7
Stipulated DC - multiple step dimming | DC-step | 0.8
Stipulated DC - ON/OFF | DC-on/off | 0.9
Stipulated Occupancy Sensor (OS) | OS | 0.7
Stipulated OS w/DC - continuous dimming | OS-cont | 0.6
Stipulated OS w/DC - multiple step dimming | OS-step | 0.65
Stipulated OS w/DC - ON/OFF | OS-on/off | 0.65
Interactive Demand and Energy Savings
(Interactive savings are added to all stipulated building types except Parking Stucture)
Building Type | Interactive HVAC Demand Savings | Interactive HVAC Energy Savings
Stipulated Office | 10% | 5%
Stipulated Non-24-Hour Supermarket/Retail/Restaurant | 10% | 5%
Stipulated Education (K-12; no summer session) | 10% | 5%
Stipulated 24-Hour Supermarket/Retail | 10% | 5%
Stipulated In-Patient Health Care | 10% | 5%
Higher Education (College / University) | 10% | 5%
Multi-Family Housing, Common Areas | 10% | 5%
Parking Structure | 0% | 0%
Conditioned Space List | Interactive HVAC Demand Savings | Interactive HVAC Energy Savings
Yes | 10% | 5%
No | 1.1 | 1.05
AC_Type
Electric Refrigerated
Other
None

## Fixture Descriptions
SORTED by | [5 empty] | Regulation
FIXTURE | LAMP |  |  | LAMP/ | WATT/ | WATT/
CODE | CODE | DESCRIPTION | BALLAST | FIXT | LAMP | FIXT
CF |  | Compact Fluorescent Fixtures
CF11/1-SCRW | CF11W | Compact Fluorescent, (1) 11W screw-in lamp/base w/ permanent locking device, any bulb shape | Mag. or Elec. | 1 | 11 | 11
CF13/1-SCRW | CF13W | Compact Fluorescent, (1) 13W screw-in lamp/base w/ permanent locking device, any bulb shape | Mag. or Elec. | 1 | 13 | 13
CF14/1-SCRW | CF14W | Compact Fluorescent, (1) 14W screw-in lamp/base w/ permanent locking device, any bulb shape | Mag. or Elec. | 1 | 14 | 14
CF15/1-SCRW | CF15W | Compact Fluorescent, (1) 15W screw-in lamp/base w/ permanent locking device, any bulb shape | Mag. or Elec. | 1 | 15 | 15
CF16/1-SCRW | CF16W | Compact Fluorescent, (1) 16W screw-in lamp/base w/ permanent locking device, any bulb shape | Mag. or Elec. | 1 | 16 | 16
CF17/1-SCRW | CF17W | Compact Fluorescent, (1) 17W screw-in lamp/base w/ permanent locking device, any bulb shape | Mag. or Elec. | 1 | 17 | 17
CF18/1-SCRW | CF18W | Compact Fluorescent, (1) 18W screw-in lamp/base w/ permanent locking device, any bulb shape | Mag. or Elec. | 1 | 18 | 18
CF2/1-SCRW | CF2W | Compact Fluorescent, (1) 2W screw-in lamp/base w/ permanent locking device, any bulb shape | Mag. or Elec. | 1 | 2 | 2
CF20/1-SCRW | CF20W | Compact Fluorescent, (1) 20W screw-in lamp/base w/ permanent locking device, any bulb shape | Mag. or Elec. | 1 | 20 | 20
CF23/1-SCRW | CF23W | Compact Fluorescent, (1) 23W screw-in lamp/base w/ permanent locking device, any bulb shape | Mag. or Elec. | 1 | 23 | 23
CF25/1-SCRW | CF25W | Compact Fluorescent, (1) 25W screw-in lamp/base w/ permanent locking device, any bulb shape | Mag. or Elec. | 1 | 25 | 25
CF26/1-SCRW | CF26W | Compact Fluorescent, (1)26W screw-in lamp/base w/ permanent locking device, any bulb shape | Mag. or Elec. | 1 | 26 | 26
CF27/1-SCRW | CF27W | Compact Fluorescent, (1) 27W screw-in lamp/base w/ permanent locking device, any bulb shape | Mag. or Elec. | 1 | 27 | 27
CF28/1-SCRW | CF28W | Compact Fluorescent, (1) 28W screw-in lamp/base w/ permanent locking device, any bulb shape | Mag. or Elec. | 1 | 28 | 28
CF32/1-SCRW | CF32W | Compact Fluorescent, (1) 32W screw-in lamp/base w/ permanent locking device, any bulb shape | Mag. or Elec. | 1 | 32 | 32
CF4/1-SCRW | CF4W | Compact Fluorescent, (1) 4W screw-in lamp/base w/ permanent locking device, any bulb shape | Mag. or Elec. | 1 | 4 | 4
CF42/1-SCRW | CF42W | Compact Fluorescent, (1) 42W screw-in lamp/base w/ permanent locking device, any bulb shape | Mag. or Elec. | 1 | 42 | 42
CF44/1-SCRW | CF44W | Compact Fluorescent, (1)44W screw-in lamp/base w/ permanent locking device, any bulb shape | Mag. or Elec. | 1 | 44 | 44
CF7/1-SCRW | CF7W | Compact Fluorescent, (1) 7W screw-in lamp/base w/ permanent locking device, any bulb shape | Mag. or Elec. | 1 | 7 | 7
CF9/1-SCRW | CF9W | Compact Fluorescent, (1) 9W screw-in lamp/base w/ permanent locking device, any bulb shape | Mag. or Elec. | 1 | 9 | 9
CFD10/1 | CFD10W | Compact Fluorescent, 2D, (1) 10W lamp | Mag-STD | 1 | 10 | 16
CFD16/1 | CFD16W | Compact Fluorescent, 2D, (1) 16W lamp | Mag-STD | 1 | 16 | 26
CFD21/1 | CFD21W | Compact Fluorescent, 2D, (1) 21W lamp | Mag-STD | 1 | 21 | 26
CFD28/1 | CFD28W | Compact Fluorescent, 2D, (1) 28W lamp | Mag-STD | 1 | 28 | 35
CFD38/1 | CFD38W | Compact Fluorescent, 2D, (1) 38W lamp | Mag-STD | 1 | 38 | 46
CFM13/1-L | CFM13W | Compact Fluorescent, Multi, 4-pin, (1) 13W lamp | Electronic | 1 | 13 | 16
CFM13/2-L | CFM13W | Compact Fluorescent, Multi, 4-pin, (2) 13W lamps | Electronic | 2 | 13 | 30
CFM18/1-L | CFM18W | Compact Fluorescent, Multi, 4-pin, (1) 18W lamp | Electronic | 1 | 18 | 20
CFM18/2-L | CFM18W | Compact Fluorescent, Multi, 4-pin, (2) 18W lamps | Electronic | 2 | 18 | 40
CFM26/1-L | CFM26W | Compact Fluorescent, Multi, 4-pin, (1) 26W lamp | Electronic | 1 | 26 | 29
CFM26/2-L | CFM26W | Compact Fluorescent, Multi, 4-pin, (2) 26W lamps | Electronic | 2 | 26 | 51
CFM32/1-L | CFM32W | Compact Fluorescent, Multi, 4-pin, (1) 42W lamps, | Electronic | 1 | 32 | 35
CFM42/1-L | CFM42W | Compact Fluorescent, Multi, 4-pin, (1) 42W lamps | Electronic | 1 | 42 | 48
CFM42/2-L | CFM42W | Compact Fluorescent, Multi, 4-pin, (2) 42W lamps | Electronic | 2 | 42 | 93
CFM42/8-L | CFM42W | Compact Fluorescent, Multi, 4-pin, (8) 42W lamps, (4) 2-lamp ballasts | Electronic | 8 | 42 | 372
CFQ10/1 | CFQ10W | Compact Fluorescent, quad, (1) 10W lamp | Mag-STD | 1 | 10 | 15
CFQ13/1 | CFQ13W | Compact Fluorescent, quad, (1) 13W lamp | Mag-STD | 1 | 13 | 17
CFQ13/1-L | CFQ13W | Compact Fluorescent, quad, (1) 13W lamp, BF=1.05 | Electronic | 1 | 13 | 15
CFQ13/2 | CFQ13W | Compact Fluorescent, quad, (2) 13W lamps | Mag-STD | 2 | 13 | 31
CFQ13/2-L | CFQ13W | Compact Fluorescent, quad, (2) 13W lamps, BF=1.0 | Electronic | 2 | 13 | 28
CFQ13/3 | CFQ13W | Compact Fluorescent, quad, (3) 13W lamps | Mag-STD | 3 | 13 | 48
CFQ15/1 | CFQ15W | Compact Fluorescent, quad, (1) 15W lamp | Mag-STD | 1 | 15 | 20
CFQ17/1 | CFQ17W | Compact Fluorescent, quad, (1) 17W lamp | Mag-STD | 1 | 17 | 24
CFQ17/2 | CFQ17W | Compact Fluorescent, quad, (2) 17W lamps | Mag-STD | 2 | 17 | 48
CFQ18/1 | CFQ18W | Compact Fluorescent, quad, (1) 18W lamp | Mag-STD | 1 | 18 | 26
CFQ18/1-L | CFQ18W | Compact Fluorescent, quad, (1) 18W lamp, BF=1.0 | Electronic | 1 | 18 | 20
CFQ18/2 | CFQ18W | Compact Fluorescent, quad, (2) 18W lamps | Mag-STD | 2 | 18 | 45
CFQ18/2-L | CFQ18W | Compact Fluorescent, quad, (2) 18W lamp, BF=1.0 | Electronic | 2 | 18 | 38
CFQ18/4 | CFQ18W | Compact Fluorescent, quad, (4) 18W lamps | Mag-STD | 2 | 18 | 90
CFQ20/1 | CFQ20W | Compact Fluorescent, quad, (1) 20W lamp | Mag-STD | 1 | 20 | 23
CFQ20/2 | CFQ20W | Compact Fluorescent, quad, (2) 20W lamps | Mag-STD | 2 | 20 | 46
CFQ22/1 | CFQ22W | Compact Fluorescent, Quad, (1) 22W lamp | Mag-STD | 1 | 22 | 24
CFQ22/2 | CFQ22W | Compact Fluorescent, Quad, (2) 22W lamps | Mag-STD | 2 | 22 | 48
CFQ22/3 | CFQ22W | Compact Fluorescent, Quad, (3) 22W lamps | Mag-STD | 3 | 22 | 72
CFQ23/1 | CFQ23W | Compact Fluorescent, Quad, (1) 23W lamp | Mag-STD | 1 | 23 | 27
CFQ25/1 | CFQ25W | Compact Fluorescent, Quad, (1) 25W lamp | Mag-STD | 1 | 25 | 33
CFQ25/2 | CFQ25W | Compact Fluorescent, Quad, (2) 25W lamps | Mag-STD | 2 | 25 | 66
CFQ26/1 | CFQ26W | Compact Fluorescent, quad, (1) 26W lamp | Mag-STD | 1 | 26 | 33
CFQ26/1-L | CFQ26W | Compact Fluorescent, quad, (1) 26W lamp, BF=0.95 | Electronic | 1 | 26 | 27
CFQ26/2 | CFQ26W | Compact Fluorescent, quad, (2) 26W lamps | Mag-STD | 2 | 26 | 66
CFQ26/2-L | CFQ26W | Compact Fluorescent, quad, (2) 26W lamps, BF=0.95 | Electronic | 2 | 26 | 50
CFQ26/3 | CFQ26W | Compact Fluorescent, quad, (3) 26W lamps | Mag-STD | 3 | 26 | 99
CFQ26/6-L | CFQ26W | Compact Fluorescent, quad, (6) 26W lamps, BF=0.95 | Electronic | 6 | 26 | 150
CFQ28/1 | CFQ28W | Compact Fluorescent, quad, (1) 28W lamp | Mag-STD | 1 | 28 | 33
CFQ28/1-L | CFQ28W | Compact Fluorescent, quad, (1) 28W lamp | Electronic | 1 | 28 | 31
CFQ28/2-L | CFQ28W | Compact Fluorescent, quad, (2) 28W lamps | Electronic | 2 | 28 | 60
CFQ9/1 | CFQ9W | Compact Fluorescent, Quad, (1) 9W lamp | Mag-STD | 1 | 9 | 14
CFQ9/2 | CFQ9W | Compact Fluorescent, Quad, (2) 9W lamps | Mag-STD | 2 | 9 | 23
CFT13/1 | CFT13W | Compact Fluorescent, twin, (1) 13W lamp | Mag-STD | 1 | 13 | 17
CFT13/1-L | CFT13W | Compact Fluorescent, twin, (1) 13W lamp | Electronic | 1 | 13 | 15
CFT13/2 | CFT13W | Compact Fluorescent, twin, (2) 13W lamps | Mag-STD | 2 | 13 | 31
CFT13/2-L | CFT13W | Compact Fluorescent, twin, (2) 13W lamps | Electronic | 2 | 13 | 28
CFT13/3 | CFT13W | Compact Fluorescent, twin, (3) 13 W lamps | Mag-STD | 3 | 13 | 48
CFT18/1 | CFT18W | Compact Fluorescent, Long twin., (1) 18W lamp | Mag-STD | 1 | 18 | 24
CFT18/1-L | CFT18W | Compact Fluorescent, twin, (1) 18W lamp | Electronic | 1 | 18 | 20
CFT18/2 | CFT18W | Compact Fluorescent, twin, (2) 18 W lamps | Mag-STD | 2 | 18 | 38
CFT22/1 | CFT22W | Compact Fluorescent, twin, (1) 22W lamp | Mag-STD | 1 | 22 | 27
CFT22/2 | CFT22W | Compact Fluorescent, twin, (2) 22W lamps | Mag-STD | 2 | 22 | 54
CFT22/4 | CFT22W | Compact Fluorescent, twin, (4) 22W lamps | Mag-STD | 4 | 22 | 108
CFT24/1 | CFT24W | Compact Fluorescent, long twin, (1) 24W lamp | Mag-STD | 1 | 24 | 32
CFT26/1 | CFT26W | Compact Fluorescent, twin, (1) 26W lamp | Mag-STD | 1 | 26 | 32
CFT26/1-L | CFT26W | Compact Fluorescent, twin, (1) 26W lamp | Electronic | 1 | 26 | 27
CFT26/2-L | CFT26W | Compact Fluorescent, twin, (2) 26W lamps | Electronic | 2 | 26 | 51
CFT28/1 | CFT28W | Compact Fluorescent, twin, (1) 28W lamp | Mag-STD | 1 | 28 | 33
CFT28/2 | CFT28W | Compact Fluorescent, twin, (2) 28W lamps | Mag-STD | 2 | 28 | 66
CFT32/1-L | CFM32W | Compact Fluorescent, twin or multi, (1) 32W lamp | Electronic | 1 | 32 | 34
CFT32/2-L | CFM32W | Compact Fluorescent, twin or multi, (2) 32W lamps | Electronic | 2 | 32 | 62
CFT32/6-L | CFM32W | Compact Fluorescent, twin or multi, (2) 32W lamps | Electronic | 6 | 32 | 186
CFT36/1 | CFT36W | Compact Fluorescent, long twin, (1) 36W lamp | Mag-STD | 1 | 36 | 51
CFT40/1 | CFT40W | Compact Fluorescent, long twin, (1) 40W lamp | Mag-STD | 1 | 40 | 46
CFT40/1-L | CFT40W | Compact Fluorescent, long twin, (1) 40W lamp | Electronic | 1 | 40 | 43
CFT40/2 | CFT40W | Compact Fluorescent, long twin, (2) 40W lamps | Mag-STD | 2 | 40 | 85
CFT40/2-L | CFT40W | Compact Fluorescent, long twin, (2) 40W lamps | Electronic | 2 | 40 | 72
CFT40/3 | CFT40W | Compact Fluorescent, long twin, (3) 40 W lamps | Mag-STD | 3 | 40 | 133
CFT40/3-L | CFT40W | Compact Fluorescent, long twin, (3) 40W lamps | Electronic | 3 | 40 | 105
CFT5/1 | CFT5W | Compact Fluorescent, twin, (1) 5W lamp | Mag-STD | 1 | 5 | 9
CFT5/2 | CFT5W | Compact Fluorescent, twin, (2) 5W lamps | Mag-STD | 2 | 5 | 18
CFT55/1-L | CFT55W | Compact Fluorescent, twin, (1) 55W lamp | Electronic | 1 | 55 | 60
CFT55/2-L | CFT55W | Compact Fluorescent, twin, (2) 55W lamps | Electronic | 2 | 55 | 110
CFT55/3-L | CFT55W | Compact Fluorescent, twin, (3) 55W lamps | Electronic | 3 | 55 | 170
CFT55/4-L | CFT55W | Compact Fluorescent, twin, (4) 55W lamps | Electronic | 4 | 55 | 220
CFT7/1 | CFT7W | Compact Fluorescent, twin, (1) 7W lamp | Mag-STD | 1 | 7 | 10
CFT7/2 | CFT7W | Compact Fluorescent, twin, (2) 7W lamps | Mag-STD | 2 | 7 | 21
CFT9/1 | CFT9W | Compact Fluorescent, twin, (1) 9W lamp | Mag-STD | 1 | 9 | 12
CFT9/2 | CFT9W | Compact Fluorescent, twin, (2) 9W lamps | Mag-STD | 2 | 9 | 23
CFT9/3 | CFT9W | Compact Fluorescent, twin, (3) 9 W lamps | Mag-STD | 3 | 9 | 34
ECF |  | EXIT Sign Fixtures
ECF5/1 | CFT5W | EXIT Compact Fluorescent, (1) 5W lamp | Mag-STD | 1 | 5 | 9
ECF5/2 | CFT5W | EXIT Compact Fluorescent, (2) 5W lamps | Mag-STD | 2 | 5 | 20
ECF6/1 | CFT6W | EXIT Compact Fluorescent, (1) 6W lamp | Mag-STD | 1 | 6 | 13
ECF6/2 | CFT6W | EXIT Compact Fluorescent, (2) 6W lamps, (2) ballasts | Mag-STD | 2 | 6 | 26
ECF7/1 | CFT7W | EXIT Compact Fluorescent, (1) 7W lamp | Mag-STD | 1 | 7 | 10
ECF7/2 | CFT7W | EXIT Compact Fluorescent, (2) 7W lamps | Mag-STD | 2 | 7 | 21
ECF9/1 | CFT9W | EXIT Compact Fluorescent, (1) 9W lamp | Mag-STD | 1 | 9 | 12
ECF9/2 | CFT9W | EXIT Compact Fluorescent, (2) 9W lamps | Mag-STD | 2 | 9 | 20
EF2/2 | F2T1 | EXIT Sub-miniature T-1 Fluorescent, (2) lamps | Electronic | 2 | 2 | 5
EF6/1 | F6T5 | EXIT Miniature Bi-pin Fluorescent, (1) 6W lamp, (1) ballast | Mag-STD | 1 | 6 | 9
EF6/2 | F6T5 | EXIT Miniature Bi-pin Fluorescent, (2) 6W lamps, (2) ballasts | Mag-STD | 2 | 6 | 18
EF8/1 | F8T5 | EXIT T5 Fluorescent, (1) 8W lamp | Mag-STD | 1 | 8 | 12
EF8/2 | F8T5 | EXIT T5 Fluorescent, (2) 8W lamps | Mag-STD | 2 | 8 | 24
EI10/2 | I10 | EXIT Incandescent, (2) 10W lamps |  | 2 | 10 | 20
EI15/1 | I15 | EXIT Incandescent, (1) 15W lamp |  | 1 | 15 | 15
EI15/2 | I15 | EXIT Incandescent, (2) 15W lamps |  | 2 | 15 | 30
EI20/1 | I20 | EXIT Incandescent, (1) 20W lamp |  | 1 | 20 | 20
EI20/2 | I20 | EXIT Incandescent, (2) 20W lamps |  | 2 | 20 | 40
EI25/1 | I25 | EXIT Incandescent, (1) 25W lamp |  | 1 | 25 | 25
EI25/2 | I25 | EXIT Incandescent, (2) 25W lamps |  | 2 | 25 | 50
EI34/1 | I34 | EXIT Incandescent, (1) 34W lamp |  | 1 | 34 | 34
EI34/2 | I34 | EXIT Incandescent, (2) 34W lamps |  | 2 | 34 | 68
EI40/1 | I40 | EXIT Incandescent, (1) 40W lamp |  | 1 | 40 | 40
EI40/2 | I40 | EXIT Incandescent, (2) 40W lamps |  | 2 | 40 | 80
EI5/1 | I5 | EXIT Incandescent, (1) 5W lamp |  | 1 | 5 | 5
EI5/2 | I5 | EXIT Incandescent, (2) 5W lamps |  | 2 | 5 | 10
EI50/2 | I50 | EXIT Incandescent, (2) 50W lamps |  | 2 | 50 | 100
EI6/1 | 6S6 | EXIT Incandescent, (1) 6 W lamp |  | 1 | 6 | 6
EI6/2 | 6S6 | EXIT Incandescent, (2) 6 W lamps |  | 2 | 6 | 12
EI7.5/1 | I7.5 | EXIT Tungsten, (1) 7.5 W lamp |  | 1 | 7.5 | 8
EI7.5/2 | I7.5 | EXIT Tungsten, (2) 7.5 W lamps |  | 2 | 7.5 | 15
ELED2/1 | LED2W | EXIT Light Emmitting Diode, (1) 2W lamp, Single Sided |  | 1 | 2 | 6
ELED2/2 | LED2W | EXIT Light Emmitting Diode, (2) 2W lamps, Dual Sided |  | 2 | 2 | 9
ELED3 | LED3W | EXIT Light Emmitting Diode, 3W |  | 1 | 3 | 3
F |  | Linear Fluorescent Fixtures
FT8 |  | T8 Linear Fluorescent Systems
F1.51LS | F15T8 | Fluorescent, (1) 18" T-8 lamp | Mag-STD | 1 | 15 | 19
F1.52LS | F15T8 | Fluorescent, (2) 18" T-8 lamps | Mag-STD | 2 | 15 | 36
F21ILL | F17T8 | Fluorescent, (1) 24", T-8 lamp, Instant Start Ballast, NLO (0.85 < BF < 0.95) | Electronic | 1 | 17 | 18
F21ILL/T2 | F17T8 | Fluorescent, (1) 24", T-8 lamp, Tandem 2-lamp IS Ballast, NLO (0.85 < BF < 0.95) | Electronic | 1 | 17 | 16.5
F21ILL/T2-R | F17T8 | Fluorescent, (1) 24", T-8 lamp, Tandem 2-lamp IS Ballast, RLO (BF< 0.85) | Electronic | 1 | 17 | 15
F21ILL/T3 | F17T8 | Fluorescent, (1) 24", T-8 lamp, Tandem 3-lamp IS Ballast, NLO (0.85 < BF < 0.95) | Electronic | 1 | 17 | 15.6667
F21ILL/T3-R | F17T8 | Fluorescent, (1) 24", T-8 lamp, Tandem 3-lamp IS Ballast, RLO (BF< 0.85) | Electronic | 1 | 17 | 13.6667
F21ILL/T4 | F17T8 | Fluorescent, (1) 24", T-8 lamp, Tandem 4-lamp IS Ballast, NLO (0.85 < BF < 0.95) | Electronic | 1 | 17 | 14.75
F21ILL/T4-R | F17T8 | Fluorescent, (1) 24", T-8 lamp, Tandem 4-lamp IS Ballast, RLO (BF< 0.85) | Electronic | 1 | 17 | 13.25
F21ILL-R | F17T8 | Fluorescent, (1) 24", T-8 lamp, Instant Start Ballast, RLO (BF< 0.85) | Electronic | 1 | 17 | 17
F21ILU | F17T8 | Fluorescent, (1) 24", T-8 lamp, Instant Start Ballast, NLO (0.85 < BF < 0.95) | Prem. Elec. | 1 | 17 | 17
F21ILU-R | F17T8 | Fluorescent, (1) 24", T-8 lamp, Instant Start Ballast, RLO (BF< 0.85) | Prem. Elec. | 1 | 17 | 15
F21LL | F17T8 | Fluorescent, (1) 24", T-8 lamp, Rapid Start Ballast, NLO (0.85 < BF < 0.95) | Electronic | 1 | 17 | 16
F21LL/T2 | F17T8 | Fluorescent, (1) 24", T-8 lamp, Tandem 2-Lamp RS Ballast, NLO (0.85 < BF < 0.95) | Electronic | 1 | 17 | 15.5
F21LL/T3 | F17T8 | Fluorescent, (1) 24", T-8 lamp, Tandem 3-Lamp RS Ballast, NLO (0.85 < BF < 0.95) | Electronic | 1 | 17 | 17.3333
F21LL/T4 | F17T8 | Fluorescent, (1) 24", T-8 lamp, Tandem 4-Lamp RS Ballast, NLO (0.85 < BF < 0.95) | Electronic | 1 | 17 | 17
F21LL-R | F17T8 | Fluorescent, (1) 24", T-8 lamp, Rapid Start Ballast, RLO (BF< 0.85) | Electronic | 1 | 17 | 15
F21SL | F17T8 | Fluorescent, (1) 24", T-8 lamp, Standard Ballast | Mag-STD | 1 | 17 | 24
F22ILL | F17T8 | Fluorescent, (2) 24", T-8 lamps, Instant Start Ballast, NLO (0.85 < BF < 0.95) | Electronic | 2 | 17 | 33
F22ILL/T4 | F17T8 | Fluorescent, (2) 24", T-8 lamps, Tandem 4-lamp IS Ballast, NLO (0.85 < BF < 0.95) | Electronic | 2 | 17 | 29.5
F22ILL/T4-R | F17T8 | Fluorescent, (2) 24", T-8 lamps, Tandem 4-lamp IS Ballast, RLO (BF<.85) | Electronic | 2 | 17 | 26.5
F22ILL-R | F17T8 | Fluorescent, (2) 24", T-8 lamps, Instant Start Ballast, RLO (BF< 0.85) | Electronic | 2 | 17 | 30
F22ILU | F17T8 | Fluorescent, (2) 24", T-8 lamps, Instant Start Ballast, NLO (0.85 < BF < 0.95) | Prem. Elec. | 2 | 17 | 30
F22ILU-R | F17T8 | Fluorescent, (2) 24", T-8 lamps, Instant Start Ballast, RLO (BF< 0.85) | Prem. Elec. | 2 | 17 | 27
F22LL | F17T8 | Fluorescent, (2) 24", T-8 lamps, Rapid Start Ballast, NLO (0.85 < BF < 0.95) | Electronic | 2 | 17 | 31
F22LL/T4 | F17T8 | Fluorescent, (2) 24", T-8 lamps, Tandem 4-lamp RS Ballast, NLO (0.85 < BF < 0.95) | Electronic | 2 | 17 | 34
F22LL-R | F17T8 | Fluorescent, (2) 24", T-8 lamps, Rapid Start Ballast, RLO (BF< 0.85) | Electronic | 2 | 17 | 28
F23ILL | F17T8 | Fluorescent, (3) 24", T-8 lamps, Instant Start Ballast, NLO (0.85 < BF < 0.95) | Electronic | 3 | 17 | 47
F23ILL-H | F17T8 | Fluorescent, (3) 24", T-8 lamps, Instant Start Ballast, HLO (0.95 < BF < 1.1) | Electronic | 3 | 17 | 51
F23ILL-R | F17T8 | Fluorescent, (3) 24", T-8 lamps, Instant Start Ballast, RLO (BF< 0.85) | Electronic | 3 | 17 | 41
F23ILU | F17T8 | Fluorescent, (3) 24", T-8 lamps, Instant Start Ballast, NLO (0.85 < BF < 0.95) | Prem. Elec. | 3 | 17 | 45
F23ILU-R | F17T8 | Fluorescent, (3) 24", T-8 lamps, Instant Start Ballast, RLO (BF< 0.85) | Prem. Elec. | 3 | 17 | 40
F23LL | F17T8 | Fluorescent, (3) 24", T-8 lamps, Rapid Start Ballast, NLO (0.85 < BF < 0.95) | Electronic | 3 | 17 | 52
F23LL-R | F17T8 | Fluorescent, (3) 24", T-8 lamps, Rapid Start Ballast, RLO (BF< 0.85) | Electronic | 3 | 17 | 41
F24ILL | F17T8 | Fluorescent, (4) 24", T-8 lamps, Instant Start Ballast, NLO (0.85 < BF < 0.95) | Electronic | 4 | 17 | 59
F24ILL-R | F17T8 | Fluorescent, (4) 24", T-8 lamps, Instant Start Ballast, RLO (BF< 0.85) | Electronic | 4 | 17 | 53
F24ILU | F17T8 | Fluorescent, (4) 24", T-8 lamps, Instant Start Ballast, NLO (0.85 < BF < 0.95) | Prem. Elec. | 4 | 17 | 57
F24ILU-R | F17T8 | Fluorescent, (4) 24", T-8 lamps, Instant Start Ballast, RLO (BF< 0.85) | Prem. Elec. | 4 | 17 | 52
F24LL | F17T8 | Fluorescent, (4) 24", T-8 lamps, Rapid Start Ballast, NLO (0.85 < BF < 0.95) | Electronic | 4 | 17 | 68
F24LL-R | F17T8 | Fluorescent, (4) 24", T-8 lamps, Rapid Start Ballast, RLO (BF< 0.85) | Electronic | 4 | 17 | 57
F31ILL | F25T8 | Fluorescent, (1) 36", T-8 lamp, Instant Start Ballast, NLO (0.85 < BF < 0.95) | Electronic | 1 | 25 | 26
F31ILL/T2 | F25T8 | Fluorescent, (1) 36", T-8 lamp, Tandem 2-lamp IS Ballast, NLO (0.85 < BF < 0.95) | Electronic | 1 | 25 | 23
F31ILL/T2-H | F25T8 | Fluorescent, (1) 36", T-8 lamp, Tandem 3-lamp IS Ballast, 1 lead capped, HLO (0.95 < BF < 1.1) | Electronic | 1 | 25 | 26
F31ILL/T2-R | F25T8 | Fluorescent, (1) 36", T-8 lamp, Tandem 2-lamp IS Ballast, RLO (BF< 0.85) | Electronic | 1 | 25 | 21
F31ILL/T3 | F25T8 | Fluorescent, (1) 36", T-8 lamp, Tandem 3-lamp IS Ballast, NLO (0.85 < BF < 0.95) | Electronic | 1 | 25 | 22.6667
F31ILL/T3-R | F25T8 | Fluorescent, (1) 36", T-8 lamp, Tandem 3-lamp IS Ballast, RLO (BF< 0.85) | Electronic | 1 | 25 | 20.3333
F31ILL/T4 | F25T8 | Fluorescent, (1) 36", T-8 lamp, Tandem 4-lamp IS Ballast, NLO (0.85 < BF < 0.95) | Electronic | 1 | 25 | 22
F31ILL/T4-R | F25T8 | Fluorescent, (1) 36", T-8 lamp, Tandem 4-lamp IS Ballast, RLO (BF< 0.85) | Electronic | 1 | 25 | 19.5
F31ILL-H | F25T8 | Fluorescent, (1) 36", T-8 lamp, Instant Start Ballast, HLO (0.95 < BF < 1.1) | Electronic | 1 | 25 | 28
F31ILL-R | F25T8 | Fluorescent, (1) 36", T-8 lamp, Instant Start Ballast, RLO (BF< 0.85) | Electronic | 1 | 25 | 22
F31ILU | F25T8 | Fluorescent, (1) 36", T-8 lamp, Instant Start Ballast, NLO (0.85 < BF < 0.95) | Prem. Elec. | 1 | 25 | 23
F31ILU/T2 | F25T8 | Fluorescent, (1) 36", T-8 lamp, Tandem 2-lamp IS Ballast, NLO (0.85 < BF < 0.95) | Prem. Elec. | 1 | 25 | 22
F31ILU/T2-R | F25T8 | Fluorescent, (1) 36", T-8 lamp, Tandem 2-lamp IS Ballast, RLO (BF< 0.85) | Prem. Elec. | 1 | 25 | 19.5
F31ILU/T3-R | F25T8 | Fluorescent, (1) 36", T-8 lamp, Tandem 3-lamp IS Ballast, RLO (BF< 0.85) | Prem. Elec. | 1 | 25 | 19.3333
F31ILU/T4-R | F25T8 | Fluorescent, (1) 36", T-8 lamp, Tandem 4-lamp IS Ballast, RLO (BF< 0.85) | Prem. Elec. | 1 | 25 | 19.25
F31ILU-R | F25T8 | Fluorescent, (1) 36", T-8 lamp, Instant Start Ballast, RLO (BF< 0.85) | Prem. Elec. | 1 | 25 | 20
F31LL | F25T8 | Fluorescent, (1) 36", T-8 lamp, Rapid Start Ballast, NLO (0.85 < BF < 0.95) | Electronic | 1 | 25 | 24
F31LL/T2 | F25T8 | Fluorescent, (1) 36", T-8 lamp, Tandem 2-lamp RS Ballast, NLO (0.85 < BF < 0.95) | Electronic | 1 | 25 | 23
F31LL/T3 | F25T8 | Fluorescent, (1) 36", T-8 lamp, Tandem 3-lamp RS Ballast, NLO (0.85 < BF < 0.95) | Electronic | 1 | 25 | 24
F31LL/T4 | F25T8 | Fluorescent, (1) 36", T-8 lamp, Tandem 4-lamp RS Ballast, NLO (0.85 < BF < 0.95) | Electronic | 1 | 25 | 22.25
F31LL-H | F25T8 | Fluorescent, (1) 36", T-8 lamp, Rapid Start Ballast, HLO (0.95 < BF < 1.1) | Electronic | 1 | 25 | 26
F31LL-R | F25T8 | Fluorescent, (1) 36", T-8 lamp, Rapid Start Ballast, RLO (BF< 0.85) | Electronic | 1 | 25 | 23
F32ILL | F25T8 | Fluorescent, (2) 36", T-8 lamps, Instant Start Ballast, NLO (0.85 < BF < 0.95) | Electronic | 2 | 25 | 46
F32ILL/2-R | F25T8 | Fluorescent, (2) 36", T-8 lamps, (2) Instant Start Ballasts, RLO (BF< 0.85) | Electronic | 2 | 25 | 44
F32ILL/T4 | F25T8 | Fluorescent, (2) 36", T-8 lamps, Tandem 4-lamp IS Ballast, NLO (0.85 < BF < 0.95) | Electronic | 2 | 25 | 44
F32ILL/T4-R | F25T8 | Fluorescent, (2) 36", T-8 lamps, Tandem 4-lamp IS Ballast, RLO (BF< 0.85) | Electronic | 2 | 25 | 39
F32ILL-H | F25T8 | Fluorescent, (2) 36", T-8 lamps, Instant Start Ballast, HLO (0.95 < BF < 1.1) | Electronic | 2 | 25 | 52
F32ILL-R | F25T8 | Fluorescent, (2) 36", T-8 lamps, Instant Start Ballast, RLO (BF< 0.85) | Electronic | 2 | 25 | 42
F32ILU | F25T8 | Fluorescent, (2) 36", T-8 lamps, Instant Start Ballast, NLO (0.85 < BF < 0.95) | Prem. Elec. | 2 | 25 | 44
F32ILU/T4-R | F25T8 | Fluorescent, (2) 36", T-8 lamps, Tandem 4-lamp IS Ballast, RLO (BF< 0.85) | Prem. Elec. | 2 | 25 | 38.5
F32ILU-R | F25T8 | Fluorescent, (2) 36", T-8 lamps, Instant Start Ballast, RLO (BF< 0.85) | Prem. Elec. | 2 | 25 | 39
F32LL | F25T8 | Fluorescent, (2) 36", T-8 lamps, Rapid Start Ballast, NLO (0.85 < BF < 0.95) | Electronic | 2 | 25 | 46
F32LL/T4 | F25T8 | Fluorescent, (2) 36", T-8 lamps, Tandem 4-lamp RS Ballast, NLO (0.85 < BF < 0.95) | Electronic | 2 | 25 | 44.5
F32LL-H | F25T8 | Fluorescent, (2) 36", T-8 lamps, Rapid Start Ballast, HLO (0.95 < BF < 1.1) | Electronic | 2 | 25 | 50
F32LL-R | F25T8 | Fluorescent, (2) 36", T-8 lamps, Rapid Start Ballast, RLO (BF< 0.85) | Electronic | 2 | 25 | 42
F32LL-V | F25T8 | Fluorescent, (2) 36", T-8 lamps, Rapid Start Ballast, VHLO (BF > 1.1) | Electronic | 2 | 25 | 70
F33ILL | F25T8 | Fluorescent, (3) 36", T-8 lamps, Instant Start Ballast, NLO (0.85 < BF < 0.95) | Electronic | 3 | 25 | 68
F33ILL-R | F25T8 | Fluorescent, (3) 36", T-8 lamps, Instant Start Ballast, RLO (BF< 0.85) | Electronic | 3 | 25 | 61
F33ILU | F25T8 | Fluorescent, (3) 36", T-8 lamps, Instant Start Ballast, NLO (0.85 < BF < 0.95) | Prem. Elec. | 3 | 25 | 65
F33ILU-R | F25T8 | Fluorescent, (3) 36", T-8 lamps, Instant Start Ballast, RLO (BF< 0.85) | Prem. Elec. | 3 | 25 | 58
F33LL | F25T8 | Fluorescent, (3) 36", T-8 lamps, Rapid Start Ballast, NLO (0.85 < BF < 0.95) | Electronic | 3 | 25 | 72
F33LL-R | F25T8 | Fluorescent, (3) 36", T-8 lamps, Rapid Start Ballast, RLO (BF< 0.85) | Electronic | 3 | 25 | 62
F34ILL | F25T8 | Fluorescent, (4) 36", T-8 lamps, Instant Start Ballast, NLO (0.85 < BF < 0.95) | Electronic | 4 | 25 | 88
F34ILL/2-R | F25T8 | Fluorescent, (4) 36", T-8 lamps, (2) Instant Start Ballasts, RLO (BF< 0.85) | Electronic | 4 | 25 | 84
F34ILL-R | F25T8 | Fluorescent, (4) 36", T-8 lamps, Instant Start Ballast, RLO (BF< 0.85) | Electronic | 4 | 25 | 78
F34ILU | F25T8 | Fluorescent, (4) 36", T-8 lamps, Instant Start Ballast, NLO (0.85 < BF < 0.95) | Prem. Elec. | 4 | 25 | 86
F34ILU-R | F25T8 | Fluorescent, (4) 36", T-8 lamps, Instant Start Ballast, RLO (BF< 0.85) | Prem. Elec. | 4 | 25 | 77
F34LL | F25T8 | Fluorescent, (4) 36", T-8 lamps, Rapid Start Ballast, NLO (0.85 < BF < 0.95) | Electronic | 4 | 25 | 89
F34LL-R | F25T8 | Fluorescent, (4) 36", T-8 lamps, Rapid Start Ballast, RLO (BF< 0.85) | Electronic | 4 | 25 | 84
F36ILL/2 | F25T8 | Fluorescent, (6) 36", T-8 lamps, (2) Instant Start Ballasts, NLO (0.85 < BF < 0.95) | Electronic | 6 | 25 | 135
F36ILL/2-R | F25T8 | Fluorescent, (6) 36", T-8 lamps, (2) Instant Start Ballasts, RLO (BF< 0.85) | Electronic | 6 | 25 | 121
F41GELL | F32T8-30W | Flourescent (1) 48" T-8 @ 30W lamp, Prog. Start or PRS Ballast, NLO (0.85 < BF < 0.95) | PRS Elec. | 1 | 30 | 28
F41GELL-R | F32T8-30W | Flourescent (1) 48" T-8 @ 30W lamp, Prog. Start or PRS Ballast, RLO (BF < 0.85) | PRS Elec. | 1 | 30 | 24
F41GLL | F32T8 | Flourescent (1) 48" T-8 lamp, Prog. Start or PRS Ballast, NLO (0.85 < BF < 0.95) | PRS Elec. | 1 | 32 | 30
F41GLL-R | F32T8 | Flourescent (1) 48" T-8 lamp, Prog. Start or PRS Ballast, RLO (BF< 0.85) | PRS Elec. | 1 | 32 | 25
F41GRLL | F28T8-28W | Flourescent (1) 48" T-8 @ 28W lamp, Prog. Start or PRS Ballast, NLO (0.85 < BF < 0.95) | PRS Elec. | 1 | 28 | 26
F41GRLL-R | F28T8-28W | Flourescent (1) 48" T-8 @ 28W lamp, Prog. Start or PRS Ballast, RLO (BF< 0.85) | PRS Elec. | 1 | 28 | 22
F41IELL | F32T8-30W | Fluorescent (1) 48" T-8 @ 30W lamp, Instant Start Ballast, NLO (0.85 < BF < 0.95) | Electronic | 1 | 30 | 29
F41IELL/T2 | F32T8-30W | Fluorescent (1) 48" T-8 @ 30W lamp, Tandem 2-lamp IS Ballast, NLO (0.85 < BF < 0.95) | Electronic | 1 | 30 | 27.5
F41IELL/T3 | F32T8-30W | Fluorescent (1) 48" T-8 @ 30W lamp, Tandem 3-lamp IS Ballast, NLO (0.85 < BF < 0.95) | Electronic | 1 | 30 | 27
F41IELL/T4 | F32T8-30W | Fluorescent (1) 48" T-8 @ 30W lamp, Tandem 4-lamp IS Ballast, NLO (0.85 < BF < 0.95) | Electronic | 1 | 30 | 26.5
F41IELL-H | F32T8-30W | Flourescent (1) 48" T-8 @ 30W lamp, Instant Start Ballast, HLO (0.95 < BF < 1.1) | Electronic | 1 | 30 | 34
F41IELL-R | F32T8-30W | Flourescent (1) 48" T-8 @ 30W lamp, Instant Start Ballast, RLO (BF < 0.85) | Electronic | 1 | 30 | 26
F41IELU | F32T8-30W | Fluorescent, (1) 48", T-8 @ 30W lamp, Instant Start Ballast, NLO (0.85 < BF < 0.95) | Prem. Elec. | 1 | 30 | 27
F41IELU/T2 | F32T8-30W | Fluorescent (1) 48" T-8 @ 30W lamp, Tandem 2-lamp IS Ballast, NLO (0.85 < BF < 0.95) | Prem. Elec. | 1 | 30 | 26
F41IELU/T2-R | F32T8-30W | Fluorescent (1) 48" T-8 @ 30W lamp, Tandem 2-lamp IS Ballast, RLO (BF< 0.85) | Prem. Elec. | 1 | 30 | 22.5
F41IELU/T3 | F32T8-30W | Fluorescent (1) 48" T-8 @ 30W lamp, Tandem 3-lamp IS Ballast, NLO (0.85 < BF < 0.95) | Prem. Elec. | 1 | 30 | 25.6667
F41IELU/T3-R | F32T8-30W | Fluorescent (1) 48" T-8 @ 30W lamp, Tandem 3-lamp IS Ballast, RLO (BF< 0.85) | Prem. Elec. | 1 | 30 | 22.6667
F41IELU/T4 | F32T8-30W | Fluorescent (1) 48" T-8 @ 30W lamp, Tandem 4-lamp IS Ballast, NLO (0.85 < BF < 0.95) | Prem. Elec. | 1 | 30 | 25.25
F41IELU/T4-R | F32T8-30W | Fluorescent (1) 48" T-8 @ 30W lamp, Tandem 4-lamp IS Ballast, RLO (BF< 0.85) | Prem. Elec. | 1 | 30 | 22.25
F41IELU-H | F32T8-30W | Fluorescent (1) 48" T-8 @ 30W lamp, Instant Start Ballast, HLO (0.95 < BF < 1.1) | Prem. Elec. | 1 | 30 | 32
F41IELU-R | F32T8-30W | Fluorescent (1) 48" T-8 @ 30W lamp, Instant Start Ballast, RLO (BF< 0.85) | Prem. Elec. | 1 | 30 | 24
F41ILL | F32T8 | Fluorescent, (1) 48", T-8 lamp, Instant Start Ballast, NLO (0.85 < BF < 0.95) | Electronic | 1 | 32 | 31
F41ILL/T2 | F32T8 | Fluorescent, (1) 48", T-8 lamp, Tandem 2-lamp IS Ballast, NLO (0.85 < BF < 0.95) | Electronic | 1 | 32 | 29
F41ILL/T2-H | F32T8 | Fluorescent, (1) 48", T-8 lamp, Tandem 3-lamp IS Ballast, 1 lead capped, HLO (0.95 < BF < 1.1) | Electronic | 1 | 32 | 33
F41ILL/T2-R | F32T8 | Fluorescent, (1) 48", T-8 lamp, Tandem 2-lamp IS Ballast, RLO (BF< 0.85) | Electronic | 1 | 32 | 25.5
F41ILL/T3 | F32T8 | Fluorescent, (1) 48", T-8 lamp, Tandem 3-lamp IS Ballast, NLO (0.85 < BF < 0.95) | Electronic | 1 | 32 | 28.3333
F41ILL/T3-H | F32T8 | Fluorescent, (1) 48", T-8 lamp, Tandem 4-lamp IS Ballast, 1 lead capped, HLO (0.95 < BF < 1.1) | Electronic | 1 | 32 | 31
F41ILL/T3-R | F32T8 | Fluorescent, (1) 48", T-8 lamp, Tandem 3-lamp IS Ballast, RLO (BF< 0.85) | Electronic | 1 | 32 | 25.3333
F41ILL/T4 | F32T8 | Fluorescent, (1) 48", T-8 lamp, Tandem 4-lamp IS Ballast, NLO (0.85 < BF < 0.95) | Electronic | 1 | 32 | 28
F41ILL/T4-R | F32T8 | Fluorescent, (1) 48", T-8 lamp, Tandem 4-lamp IS Ballast, RLO (BF< 0.85) | Electronic | 1 | 32 | 24.5
F41ILL-H | F32T8 | Fluorescent, (1) 48", T-8 lamp, Instant Start Ballast, HLO (0.95 < BF < 1.1) | Electronic | 1 | 32 | 36
F41ILL-R | F32T8 | Fluorescent, (1) 48", T-8 lamp, Instant Start Ballast, RLO (BF< 0.85) | Electronic | 1 | 32 | 27
F41ILU | F32T8 | Fluorescent, (1) 48", T-8 lamp, Instant Start Ballast, NLO (0.85 < BF < 0.95) | Prem. Elec. | 1 | 32 | 28
F41ILU/T2 | F32T8 | Fluorescent, (1) 48", T-8 lamp, Tandem 2-lamp IS Ballast, NLO (0.85 < BF < 0.95) | Prem. Elec. | 1 | 32 | 27
F41ILU/T2-R | F32T8 | Fluorescent, (1) 48", T-8 lamp, Tandem 2-lamp IS Ballast, RLO (BF< 0.85) | Prem. Elec. | 1 | 32 | 24
F41ILU/T3 | F32T8 | Fluorescent, (1) 48", T-8 lamp, Tandem 3-lamp IS Ballast, NLO (0.85 < BF < 0.95) | Prem. Elec. | 1 | 32 | 27
F41ILU/T3-R | F32T8 | Fluorescent, (1) 48", T-8 lamp, Tandem 3-lamp IS Ballast, RLO (BF< 0.85) | Prem. Elec. | 1 | 32 | 24
F41ILU/T4 | F32T8 | Fluorescent, (1) 48", T-8 lamp, Tandem 4-lamp IS Ballast, NLO (0.85 < BF < 0.95) | Prem. Elec. | 1 | 32 | 26.75
F41ILU/T4-R | F32T8 | Fluorescent, (1) 48", T-8 lamp, Tandem 4-lamp IS Ballast, RLO (BF< 0.85) | Prem. Elec. | 1 | 32 | 23.75
F41ILU-H | F32T8 | Fluorescent, (1) 48", T-8 lamp, Instant Start Ballast, HLO (0.95 < BF < 1.1) | Prem. Elec. | 1 | 32 | 35
F41ILU-R | F32T8 | Fluorescent, (1) 48", T-8 lamp, Instant Start Ballast, RLO (BF< 0.85) | Prem. Elec. | 1 | 32 | 25
F41IRLL | F28T8-28W | Fluorescent, (1) 48", T-8 @ 28W lamp, Instant Start Ballast, NLO (0.85 < BF < 0.95) | Electronic | 1 | 28 | 27
F41IRLL-V | F28T8-28W | Fluorescent, (1) 48" T-8 @ 28W lamp, Instant Start Ballast, VHLO (BF > 1.1) | Electronic | 1 | 28 | 35
F41IRLU | F28T8-28W | Fluorescent, (1), T-8 @ 28W lamp, Instant Start Ballast, NLO (0.85 < BF < 0.95) | Prem. Elec. | 1 | 28 | 25
F41IRLU-R | F28T8-28W | Fluorescent, (1), T-8 @ 28W lamp, Instant Start Ballast, RLO (BF< 0.85) | Prem. Elec. | 1 | 28 | 22
F41LE | F32T8 | Fluorescent, (1) 48", T-8 lamp | Mag-ES | 1 | 32 | 35
F41LHL | F48T8/HO | Fluorescent, (1) 48", T-8 HO lamps, (1) Instant Start Ballast, NLO (0.85 < BF < 0.95) | Electronic | 1 | 44 | 59
F41LL | F32T8 | Fluorescent, (1) 48", T-8 lamp, Rapid Start Ballast, NLO (0.85 < BF < 0.95) | Electronic | 1 | 32 | 32
F41LL/T2 | F32T8 | Fluorescent, (1) 48", T-8 lamp, Tandem 2-lamp RS Ballast, NLO (0.85 < BF < 0.95) | Electronic | 1 | 32 | 30
F41LL/T2-H | F32T8 | Fluorescent, (1) 48", T-8 lamp, Tandem 3-lamp RS Ballast, 1 lead capped, HLO (0.95 < BF < 1.1) | Electronic | 1 | 32 | 35
F41LL/T2-R | F32T8 | Fluorescent, (1) 48", T-8 lamp, Tandem 2-lamp RS Ballast, RLO (BF< 0.85) | Electronic | 1 | 32 | 27
F41LL/T3 | F32T8 | Fluorescent, (1) 48", T-8 lamp, Tandem 3-lamp RS Ballast, NLO (0.85 < BF < 0.95) | Electronic | 1 | 32 | 31
F41LL/T3-H | F32T8 | Fluorescent, (1) 48", T-8 lamp, Tandem 4-lamp RS Ballast, 1 lead capped, HLO (0.95 < BF < 1.1) | Electronic | 1 | 32 | 32.6667
F41LL/T3-R | F32T8 | Fluorescent, (1) 48", T-8 lamp, Tandem 3-lamp RS Ballast, RLO (BF< 0.85) | Electronic | 1 | 32 | 25.3333
F41LL/T4 | F32T8 | Fluorescent, (1) 48", T-8 lamp, Tandem 4-lamp RS Ballast, NLO (0.85 < BF < 0.95) | Electronic | 1 | 32 | 29.5
F41LL/T4-R | F32T8 | Fluorescent, (1) 48", T-8 lamp, Tandem 4-lamp RS Ballast, RLO (BF< 0.85) | Electronic | 1 | 32 | 26.25
F41LL-H | F32T8 | Fluorescent, (1) 48", T-8 lamp, Rapid Start Ballast, HLO (0.95 < BF < 1.1) | Electronic | 1 | 32 | 39
F41LL-R | F32T8 | Fluorescent, (1) 48", T-8 lamp, Rapid Start Ballast, RLO (BF< 0.85) | Electronic | 1 | 32 | 27
F42GELL | F32T8-30W | Flourescent (2) 48" T-8 @ 30W lamps, Prog. Start or PRS Ballast, NLO (0.85 < BF < 0.95) | PRS Elec. | 2 | 30 | 56
F42GELL-R | F32T8-30W | Flourescent (2) 48" T-8 @ 30W lamps, Prog. Start or PRS Ballast, RLO (BF < 0.85) | PRS Elec. | 2 | 30 | 43
F42GLL | F32T8 | Flourescent (2) 48" T-8 lamps, Prog. Start or PRS Ballast, NLO (0.85 < BF < 0.95) | PRS Elec. | 2 | 32 | 59
F42GLL-R | F32T8 | Flourescent (2) 48" T-8 lamps, Prog. Start or PRS Ballast, RLO (BF < 0.85) | PRS Elec. | 2 | 32 | 47
F42GRLL | F28T8-28W | Flourescent (2) 48" T-8 @ 28W lamps, Prog. Start or PRS Ballast, NLO (0.85 < BF < 0.95) | PRS Elec. | 2 | 28 | 49
F42GRLL-R | F28T8-28W | Flourescent (2) 48" T-8 @ 28W lamps, Prog. Start or PRS Ballast, RLO (BF< 0.85) | PRS Elec. | 2 | 28 | 40
F42IELL | F32T8-30W | Fluorescent (2) 48" T-8 @ 30W lamps, Instant Start Ballast, NLO (0.85 < BF < 0.95) | Electronic | 2 | 30 | 55
F42IELL/T4 | F32T8-30W | Fluorescent (4) 48" T-8 @ 30W lamps, Tandem 4-lamp IS Ballast, NLO (0.85 < BF < 0.95) | Electronic | 2 | 30 | 53
F42IELL/T4-R | F32T8-30W | Fluorescent (4) 48" T-8 @ 30W lamps, Tandem 4-lamp IS Ballast, RLO (BF< 0.85) | Electronic | 2 | 30 | 46
F42IELL-H | F32T8-30W | Fluorescent (2) 48" T-8 @ 30W lamps, Instant Start Ballast, HLO (0.95 < BF < 1.1) | Electronic | 2 | 30 | 62
F42IELL-R | F32T8-30W | Flourescent (2) 48" T-8 @ 30W lamps, Instant Start Ballast, RLO (BF< 0.85) | Electronic | 2 | 30 | 49
F42IELU | F32T8-30W | Fluorescent (2) 48" T-8 @ 30W lamps, Instant Start Ballast, NLO (0.85 < BF < 0.95) | Prem. Elec. | 2 | 30 | 52
F42IELU/T4 | F32T8-30W | Fluorescent (2) 48" T-8 @ 30W lamps, Tandem 4-lamp IS Ballast, NLO (0.85 < BF < 0.95) | Prem. Elec. | 2 | 30 | 50.5
F42IELU/T4-R | F32T8-30W | Fluorescent (2) 48" T-8 @ 30W lamps, Tandem 4-lamp IS Ballast, RLO (BF< 0.85) | Prem. Elec. | 2 | 30 | 44.5
F42IELU-R | F32T8-30W | Fluorescent (2) 48" T-8 @ 30W lamps, Instant Start, RLO (BF< 0.85) | Prem. Elec. | 2 | 30 | 45
F42ILL | F32T8 | Fluorescent, (2) 48", T-8 lamps, Instant Start Ballast, NLO (0.85 < BF < 0.95) | Electronic | 2 | 32 | 58
F42ILL/2 | F32T8 | Fluorescent, (2) 48", T-8 lamps, (2) 1-lamp Instant Start Ballast, NLO (0.85 < BF < 0.95) | Electronic | 2 | 32 | 62
F42ILL/2-R | F32T8 | Fluorescent, (2) 48" T-8 lamps, (2) 1-lamp Instant Start Ballasts, RLO (BF< 0.85) | Electronic | 2 | 32 | 54
F42ILL/T4 | F32T8 | Fluorescent, (2) 48", T-8 lamps, Tandem 4-lamp IS Ballast, NLO (0.85 < BF < 0.95) | Electronic | 2 | 32 | 56
F42ILL/T4-R | F32T8 | Fluorescent, (2) 48", T-8 lamps, Tandem 4-lamp IS Ballast, RLO (BF< 0.85) | Electronic | 2 | 32 | 49
F42ILL-H | F32T8 | Fluorescent, (2) 48", T-8 lamp, Instant Start Ballast, HLO (0.95 < BF < 1.1) | Electronic | 2 | 32 | 66
F42ILL-R | F32T8 | Fluorescent, (2) 48", T-8 lamps, Instant Start Ballast, RLO (BF< 0.85) | Electronic | 2 | 32 | 51
F42ILL-V | F32T8 | Fluorescent, (2) 48", T-8 lamps, Instant Start Ballast, VHLO (BF > 1.1) | Electronic | 2 | 32 | 77
F42ILU | F32T8 | Fluorescent, (2) 48", T-8 lamps, Instant Start Ballast, NLO (0.85 < BF < 0.95) | Prem. Elec. | 2 | 32 | 54
F42ILU/T4 | F32T8 | Fluorescent, (2) 48", T-8 lamps, Tandem 4-lamp IS Ballast, NLO (0.85 < BF < 0.95) | Prem. Elec. | 2 | 32 | 53.5
F42ILU/T4-R | F32T8 | Fluorescent, (2) 48", T-8 lamps, Tandem 4-lamp IS Ballast, RLO (BF< 0.85) | Prem. Elec. | 2 | 32 | 47.5
F42ILU-R | F32T8 | Fluorescent, (2) 48", T-8 lamps, Instant Start, RLO (BF< 0.85) | Prem. Elec. | 2 | 32 | 48
F42IRLL | F28T8-28W | Fluorescent, (2) 48", T-8 @ 28W lamps, Instant Start Ballast, NLO (0.85 < BF < 0.95) | Electronic | 2 | 28 | 52
F42IRLL-V | F28T8-28W | Fluorescent, (2) 48" T-8 @ 28W lamps, Instant Start Ballast, VHLO (BF > 1.1) | Electronic | 2 | 28 | 68
F42IRLU | F28T8-28W | Fluorescent, (2), T-8 @ 28W lamps, Instant Start Ballast, NLO (0.85 < BF < 0.95) | Prem. Elec. | 2 | 28 | 48
F42IRLU-R | F28T8-28W | Fluorescent, (2) 48", T-8 @ 28W lamps, Instant Start Ballast, RLO (BF< 0.85) | Prem. Elec. | 2 | 28 | 43
F42IRLU-V | F28T8-28W | Fluorescent, (2) 48", T-8 @ 28W lamps, Instant Start Ballast, VHLO (BF > 1.1) | Prem. Elec. | 2 | 28 | 65
F42LE | F32T8 | Fluorescent, (2) 48", T-8 lamp | Mag-ES | 2 | 32 | 71
F42LHL | F48T8/HO | Fluorescent, (2) 48", T-8 HO lamps, (1) Instant Start Ballast, NLO (0.85 < BF < 0.95) | Electronic | 2 | 44 | 98
F42LL | F32T8 | Fluorescent, (2) 48", T-8 lamps, Rapid Start Ballast, NLO (0.85 < BF < 0.95) | Electronic | 2 | 32 | 60
F42LL/2 | F32T8 | Fluorescent, (2) 48", T-8 lamps, (2) 1-lamp Rapid Start Ballasts, NLO (0.85 < BF < 0.95) | Electronic | 2 | 32 | 64
F42LL/T4 | F32T8 | Fluorescent, (2) 48", T-8 lamps, Tandem 4-lamp RS Ballast, NLO (0.85 < BF < 0.95) | Electronic | 2 | 32 | 59
F42LL/T4-R | F32T8 | Fluorescent, (2) 48", T-8 lamp, Tandem 4-lamp RS Ballast, RLO (BF< 0.85) | Electronic | 2 | 32 | 52.5
F42LL-H | F32T8 | Fluorescent, (2) 48", T-8 lamp, Rapid Start Ballast, HLO (0.95 < BF < 1.1) | Electronic | 2 | 32 | 70
F42LL-R | F32T8 | Fluorescent, (2) 48", T-8 lamp, Rapid Start Ballast, RLO (BF< 0.85) | Electronic | 2 | 32 | 54
F42LL-V | F32T8 | Fluorescent, (2) 48", T-8 lamp, Rapid Start Ballast, VHLO (BF > 1.1) | Electronic | 2 | 32 | 85
F43GELL | F32T8-30W | Flourescent (3) 48" T-8 @ 30W lamps, Prog. Start or PRS Ballast, NLO (0.85 < BF < 0.95) | PRS Elec. | 3 | 30 | 83
F43GELL-R | F32T8-30W | Flourescent (3) 48" T-8 @ 30W lamps, Prog. Start or PRS Ballast, RLO (BF < 0.85) | PRS Elec. | 3 | 30 | 67
F43GLL | F32T8 | Flourescent (3) 48" T-8 lamps, Prog. Start or PRS Ballast, NLO (0.85 < BF < 0.95) | PRS Elec. | 3 | 32 | 88
F43GLL-R | F32T8 | Flourescent (3) 48" T-8 lamps, Prog. Start or PRS Ballast, RLO (BF < 0.85) | PRS Elec. | 3 | 32 | 72
F43GRLL | F28T8-28W | Flourescent (3) 48" T-8 @ 28W lamps, Prog. Start or PRS Ballast, NLO (0.85 < BF < 0.95) | PRS Elec. | 3 | 28 | 75
F43GRLL-R | F28T8-28W | Fluorescent, (3) 48" T-8 @ 28W lamps, Prog. Start or PRS Ballast, RLO (BF < 0.85) | PRS Elec. | 3 | 28 | 62
F43IELL | F32T8-30W | Fluorescent (3) 48" T-8 @ 30 W lamps, Instant Start Ballast, NLO (0.85 < BF < 0.95) | Electronic | 3 | 30 | 81
F43IELL/2 | F32T8-30W | Fluorescent (3) 48" T-8 @ 30 W lamps, (1) 1-lamp and (1) 2-lamp IS Ballast, NLO (0.85 < BF < 0.95) | Electronic | 3 | 30 | 84
F43IELL/2-H | F32T8-30W | Fluorescent (3) 48" T-8 @ 30 W lamps, (1) 2-lamp, (1) 3-lamp IS Ballast, 1 lead capped, HLO (0.95 < BF < 1.1) | Electronic | 3 | 30 | 96
F43IELL/2-R | F32T8-30W | Fluorescent (3) 48" T-8 @ 30 W lamps, (1) 1-lamp and (1) 2-lamp IS Ballast, RLO (BF < 0.85) | Electronic | 3 | 30 | 75
F43IELL-H | F32T8-30W | Fluorescent (3) 48" T-8 @ 30 W lamps, Instant Start Ballast, HLO (0.95 < BF < 1.1) | Electronic | 3 | 30 | 86
F43IELL-R | F32T8-30W | Fluorescent (3) 48" T-8 @ 30 W lamps, Instant Start Ballast, RLO (BF < 0.85) | Electronic | 3 | 30 | 71
F43IELU | F32T8-30W | Fluorescent (3) 48" T-8 @ 30W lamps, Instant Start Ballast, NLO (0.85 < BF < 0.95) | Prem. Elec. | 3 | 30 | 77
F43IELU-R | F32T8-30W | Fluorescent (3) 48" T-8 @ 30W lamps, Instant Start Ballast, RLO (BF < 0.85) | Prem. Elec. | 3 | 30 | 68
F43ILL | F32T8 | Fluorescent, (3) 48" T-8 lamps, Instant Start Ballast, NLO (0.85 < BF < 0.95) | Electronic | 3 | 32 | 85
F43ILL/2 | F32T8 | Fluorescent, (3) 48" T-8 lamps, (2) Instant Start Ballasts, NLO (0.85 < BF < 0.95) | Electronic | 3 | 32 | 89
F43ILL/2-H | F32T8 | Fluorescent (3) 48" T-8 lamps, (1) 2-lamp and (1) 3-lamp IS Ballast,1 lead capped, HLO (0.95 < BF < 1.1) | Electronic | 3 | 32 | 102
F43ILL/2-R | F32T8 | Fluorescent, (3) 48" T-8 lamps, (1) 1-lamp and (1) 2-lamp IS Ballast, RLO (BF < 0.85) | Electronic | 3 | 32 | 78
F43ILL-H | F32T8 | Fluorescent, (3) 48" T-8 lamps, Instant Start Ballast, HLO (0.95 < BF < 1.1) | Electronic | 3 | 32 | 93
F43ILL-R | F32T8 | Fluorescent, (3) 48" T-8 lamps, Instant Start Ballast, RLO (BF < 0.85) | Electronic | 3 | 32 | 76
F43ILL-V | F32T8 | Fluorescent, (3) 48" T-8 lamps, Instant Start Ballast, VHLO (BF > 1.1) | Electronic | 3 | 32 | 112
F43ILU | F32T8 | Fluorescent, (3) 48" T-8 lamps, Instant Start Ballast, NLO (0.85 < BF < 0.95) | Prem. Elec. | 3 | 32 | 81
F43ILU-R | F32T8 | Fluorescent, (3) 48" T-8 lamps, Instant Start Ballast, RLO (BF < 0.85) | Prem. Elec. | 3 | 32 | 72
F43IRLL | F28T8-28W | Fluorescent, (3) 48" T-8 @ 28W lamps, Instant Start Ballast, NLO (0.85 < BF < 0.95) | Electronic | 3 | 28 | 76
F43IRLL-H | F28T8-28W | Fluorescent, (3) 48" T-8 @ 28W lamps, Instant Start Ballast, HLO (.95 < BF < 1.1) | Electronic | 3 | 28 | 82
F43IRLL-V | F28T8-28W | Fluorescent, (3) 48" T-8 @ 28W lamps, Instant Start Ballast, VHLO (BF > 1.1) | Electronic | 3 | 28 | 97
F43IRLU | F28T8-28W | Fluorescent, (3) 48" T-8 lamps @ 28W, Instant Start Ballast, NLO (0.85 < BF < 0.95) | Prem. Elec. | 3 | 28 | 72
F43IRLU-R | F28T8-28W | Fluorescent, (3) 48" T-8 @ 28W lamps, Instant Start Ballast, RLO (BF < 0.85) | Prem. Elec. | 3 | 28 | 63
F43IRLU-V | F28T8-28W | Fluorescent, (3) 48" T-8 @ 28W lamps, Instant Start Ballast, VHLO (BF > 1.1) | Prem. Elec. | 3 | 28 | 96
F43LE | F32T8 | Fluorescent, (3) 48", T-8 lamp | Mag-ES | 3 | 32 | 110
F43LHL | F48T8/HO | Fluorescent, (3) 48", T-8 HO lamps, (2) Instant Start Ballasts, NLO (0.85 < BF < 0.95) | Electronic | 3 | 44 | 157
F43LL | F32T8 | Fluorescent, (3) 48", T-8 lamps, Rapid Start Ballast, NLO (0.85 < BF < 0.95) | Electronic | 3 | 32 | 93
F43LL/2 | F32T8 | Fluorescent, (3) 48", T-8 lamps, (1) 1-lamp and (1) 2-lamp RS Ballast, NLO (0.85 < BF < 0.95) | Electronic | 3 | 32 | 92
F43LL-H | F32T8 | Fluorescent, (3) 48", T-8 lamp, Rapid Start Ballast, HLO (.95 < BF < 1.1) | Electronic | 3 | 32 | 98
F43LL-R | F32T8 | Fluorescent, (3) 48", T-8 lamp, Rapid Start Ballast, RLO (BF < 0.85) | Electronic | 3 | 32 | 76
F44GELL | F32T8-30W | Flourescent (4) 48" T-8 @ 30W lamps, Prog. Start or PRS Ballast, NLO (0.85 < BF < 0.95) | PRS Elec. | 4 | 30 | 109
F44GELL-R | F32T8-30W | Flourescent (4) 48" T-8 @ 30W lamps, Prog. Start or PRS Ballast, RLO (BF < 0.85) | PRS Elec. | 4 | 30 | 86
F44GLL | F32T8 | Flourescent (4) 48" T-8 lamps, Prog. Start or PRS Ballast, NLO (0.85 < BF < 0.95) | PRS Elec. | 4 | 32 | 115
F44GLL-R | F32T8 | Flourescent (4) 48" T-8 lamps, Prog. Start or PRS Ballast, RLO (BF < 0.85) | PRS Elec. | 4 | 32 | 92
F44GRLL | F28T8-28W | Flourescent (4) 48" T-8 @ 28W lamps, Prog. Start or PRS Ballast, NLO (0.85 < BF < 0.95) | PRS Elec. | 4 | 28 | 99
F44GRLL-R | F28T8-28W | Flourescent (4) 48" T-8 @ 28W lamps, Prog. Start or PRS Ballast, RLO (BF < 0.85) | PRS Elec. | 4 | 28 | 80
F44IELL | F32T8-30W | Fluorescent (4) 48" T-8 @ 30W lamps, Instant Start Ballast, NLO (0.85 < BF < 0.95) | Electronic | 4 | 30 | 106
F44IELL/2 | F32T8-30W | Fluorescent (4) 48" T-8 @ 30W lamps, (2) 2-lamp IS Ballasts, NLO (0.85 < BF < 0.95) | Electronic | 4 | 30 | 110
F44IELL/2-H | F32T8-30W | Fluorescent (4) 48" T-8 @ 30W lamps, (2) 3-lamp IS Ballasts, 1 lead capped, HLO (.95 < BF < 1.1) | Electronic | 4 | 30 | 124
F44IELL/2-R | F32T8-30W | Fluorescent (4) 48" T-8 @ 30W lamps, (2) 2-lamp IS Ballasts, RLO (BF< 0.85) | Electronic | 4 | 30 | 98
F44IELL-R | F32T8-30W | Fluorescent (4) 48" T-8 @ 30W lamps, Instant Start Ballast, RLO (BF < 0.85) | Electronic | 4 | 30 | 92
F44IELU | F32T8-30W | Fluorescent (4) 48" T-8 @ 30W lamps, Instant Start Ballast, NLO (0.85 < BF < 0.95) | Prem. Elec. | 4 | 30 | 101
F44IELU-R | F32T8-30W | Fluorescent (4) 48" T-8 @ 30W lamps, Instant Start Ballast, RLO (BF < 0.85) | Prem. Elec. | 4 | 30 | 89
F44ILL | F32T8 | Fluorescent, (4) 48", T-8 lamps, Instant Start Ballast, NLO (0.85 < BF < 0.95) | Electronic | 4 | 32 | 112
F44ILL/2 | F32T8 | Fluorescent, (4) 48", T-8 lamps, (2) 2-lamp IS Ballasts, NLO (0.85 < BF < 0.95) | Electronic | 4 | 32 | 116
F44ILL/2-H | F32T8 | Fluorescent, (4) 48", T-8 lamps, (2) 3-lamp IS Ballasts, 1 lead capped, HLO (.95 < BF < 1.1) | Electronic | 4 | 32 | 132
F44ILL/2-R | F32T8 | Fluorescent, (4) 48", T-8 lamps, (2) 2-lamp IS Ballasts, RLO (BF < 0.85) | Electronic | 4 | 32 | 102
F44ILL/2-V | F32T8 | Fluorescent, (4) 48", T-8 lamps, (2) 2-lamp IS Ballasts, VHLO (BF > 1.1) | Electronic | 4 | 32 | 154
F44ILL-R | F32T8 | Fluorescent, (4) 48", T-8 lamps, Instant Start Ballast, RLO (BF < 0.85) | Electronic | 4 | 32 | 98
F44ILL-V | F32T8 | Fluorescent, (4) 48", T-8 lamps, Instant Start Ballast, VHLO (BF > 1.1) | Electronic | 4 | 32 | 151
F44ILU | F32T8 | Fluorescent, (4) 48", T-8 lamps, Instant Start Ballast, NLO (0.85 < BF < 0.95) | Prem. Elec. | 4 | 32 | 107
F44ILU-R | F32T8 | Fluorescent, (4) 48", T-8 lamps, Instant Start Ballast, RLO (BF < 0.85) | Prem. Elec. | 4 | 32 | 95
F44IRLL | F28T8-28W | Fluorescent, (4) 48", T-8 @ 28W lamps, Instant Start Ballast, NLO (0.85 < BF < 0.95) | Electronic | 4 | 28 | 99
F44IRLL-R | F28T8-28W | Fluorescent, (4) 48", T-8 @ 28W lamps, Instant Start Ballast, RLO (BF < 0.85) | Electronic | 4 | 28 | 85
F44IRLU | F28T8-28W | Fluorescent, (4) 48", T-8 @ 28W lamps, Instant Start Ballast, NLO (0.85 < BF < 0.95) | Prem. Elec. | 4 | 28 | 94
F44IRLU-R | F28T8-28W | Fluorescent, (4) 48" T-8 @ 28W lamps, Instant Start Ballast, RLO (BF < 0.85) | Prem. Elec. | 4 | 28 | 83
F44IRLU-V | F28T8-28W | Fluorescent, (4) 48" T-8 @ 28W lamps, Instant Start Ballast, VHLO (BF > 1.1) | Prem. Elec. | 4 | 28 | 131
F44LE | F32T8 | Fluorescent, (4) 48", T-8 lamps | Mag-ES | 4 | 32 | 142
F44LHL | F48T8/HO | Fluorescent, (4) 48", T-8 HO lamps, (2) Instant Start Ballasts, NLO (0.85 < BF < 0.95) | Electronic | 4 | 44 | 196
F44LL | F32T8 | Fluorescent, (4) 48", T-8 lamps, Rapid Start Ballast, NLO (0.85 < BF < 0.95) | Electronic | 4 | 32 | 118
F44LL/2 | F32T8 | Fluorescent, (4) 48", T-8 lamps, (2) 2-lamp Rapid Start Ballast, NLO (0.85 < BF < 0.95) | Electronic | 4 | 32 | 120
F44LL-R | F32T8 | Fluorescent, (4) 48", T-8 lamps, Rapid Start Ballast, RLO (BF < 0.85) | Electronic | 4 | 32 | 105
F45ILL/2 | F32T8 | Fluorescent, (5) 48", T-8 lamps, (1) 3-lamp and (1) 2-lamp IS ballast, NLO (0.85 < BF < 0.95) | Electronic | 5 | 32 | 143
F46GLL/2-R | F32T8 | Flourescent (6) 48" T-8 lamps, (2) Prog. Start or PRS Ballasts, RLO (BF < 0.85) | PRS Elec. | 6 | 32 | 141.5
F46IELU/2 | F32T8-30W | Fluorescent (6) 48" T-8 @ 30W lamps, (2) IS Ballasts, NLO (0.85 < BF < 0.95) | Prem. Elec. | 6 | 30 | 153.5
F46IELU/2-R | F32T8-30W | Fluorescent (6) 48" T-8 @ 30W lamps, (2) IS Ballasts, RLO (BF < 0.85) | Prem. Elec. | 6 | 30 | 135
F46ILL/2 | F32T8 | Fluorescent, (6) 48", T-8 lamps, (2) IS Ballasts, NLO (0.85 < BF < 0.95) | Electronic | 6 | 32 | 170
F46ILL/2-R | F32T8 | Fluorescent, (6) 48", T-8 lamps, (2) IS Ballasts, RLO (BF < 0.85) | Electronic | 6 | 32 | 150.5
F46ILL/2-V | F32T8 | Fluorescent (6) 48" T-8 lamps, (2) IS Ballasts, VHLO (BF > 1.1) | Electronic | 6 | 32 | 226
F46ILU/2 | F32T8 | Fluorescent (6) 48" T-8 lamps, (2) IS Ballasts, NLO (0.85 < BF < 0.95) | Prem. Elec. | 6 | 32 | 161.5
F46ILU/2-R | F32T8 | Fluorescent (6) 48" T-8 lamps, (2) IS Ballasts, RLO (BF < 0.85) | Prem. Elec. | 6 | 32 | 143.5
F46IRLU/2-R | F28T8-28W | Fluorescent (6) 48" T-8 @ 28W lamps, (2) IS Ballasts, RLO (BF < 0.85) | Prem. Elec. | 6 | 28 | 126
F46LL/2 | F32T8 | Fluorescent, (6) 48", T-8 lamps, (2) Rapid Start Ballasts, NLO (0.85 < BF < 0.95) | Electronic | 6 | 32 | 182
F48ILL/2 | F32T8 | Fluorescent, (8) 48", T-8 lamps, (2) 4-lamp IS Ballasts, NLO (0.85 < BF < 0.95) | Electronic | 8 | 32 | 224
F48ILL/2-R | F32T8 | Fluorescent, (8) 48", T-8 lamps, (2) 4-lamp IS Ballasts, RLO (BF < 0.85) | Electronic | 8 | 32 | 196
F51ILL | F40T8 | Fluorescent, (1) 60", T-8 lamp, Instant Start Ballast, NLO (0.85 < BF < 0.95) | Electronic | 1 | 40 | 36
F51ILL/T2 | F40T8 | Fluorescent, (1) 60", T-8 lamp, Tandem 2-lamp IS Ballast, NLO (0.85 < BF < 0.95) | Electronic | 1 | 40 | 36
F51ILL/T3 | F40T8 | Fluorescent, (1) 60", T-8 lamp, Tandem 3-lamp IS Ballast, NLO (0.85 < BF < 0.95) | Electronic | 1 | 40 | 35.3333
F51ILL/T4 | F40T8 | Fluorescent, (1) 60", T-8 lamp, Tandem 4-lamp IS Ballast, NLO (0.85 < BF < 0.95) | Electronic | 1 | 40 | 33.5
F51ILL-R | F40T8 | Fluorescent, (1) 60", T-8 lamp, Instant Start Ballast, RLO (BF < 0.85) | Electronic | 1 | 40 | 43
F52ILL | F40T8 | Fluorescent, (2) 60", T-8 lamps, Instant Start Ballast, NLO (0.85 < BF < 0.95) | Electronic | 2 | 40 | 72
F52ILL/T4 | F40T8 | Fluorescent, (2) 60", T-8 lamps, Tandem 4-lamp IS Ballast, NLO (0.85 < BF < 0.95) | Electronic | 2 | 40 | 67
F52ILL-H | F40T8 | Fluorescent, (2) 60", T-8 lamps, Instant Start Ballast, HLO (.95 < BF < 1.1) | Electronic | 2 | 40 | 80
F52ILL-R | F40T8 | Fluorescent, (2) 60", T-8 lamps, Instant Start Ballast, RLO (BF < 0.85) | Electronic | 2 | 40 | 73
F53ILL | F40T8 | Fluorescent, (3) 60", T-8 lamps, Instant Start Ballast, NLO (0.85 < BF < 0.95) | Electronic | 3 | 40 | 106
F53ILL-H | F40T8 | Fluorescent, (3) 60", T-8 lamps, Instant Start Ballast, HLO (.95 < BF < 1.1) | Electronic | 3 | 40 | 108
F54ILL | F40T8 | Fluorescent, (4) 60", T-8 lamps, Instant Start Ballast, NLO (0.85 < BF < 0.95) | Electronic | 4 | 40 | 134
F54ILL-H | F40T8 | Fluorescent, (4) 60", T-8 lamps, Instant Start Ballast, HLO (.95 < BF < 1.1) | Electronic | 4 | 40 | 126
F81IELU | F96T8-57W | Flourescent, (1) 96" T-8 @ 57W lamp, Instant Start Ballast, NLO (0.85 < BF < 0.95) | Prem. Elec. | 1 | 57 | 51
F81ILL | F96T8 | Fluorescent, (1) 96", T-8 lamp, Instant Start Ballast, NLO (0.85 < BF < 0.95) | Electronic | 1 | 59 | 58
F81ILL/T2 | F96T8 | Fluorescent, (1) 96", T-8 lamp, Tandem 2-lamp IS Ballast, NLO (0.85 < BF < 0.95) | Electronic | 1 | 59 | 54.5
F81ILL/T2-R | F96T8 | Fluorescent, (1) 96", T-8 lamp, Tandem 2-lamp IS Ballast, RLO (BF < 0.85) | Electronic | 1 | 59 | 49
F81ILL-H | F96T8 | Fluorescent, (1) 96", T-8 lamp, Instant Start Ballast, HLO (.95 < BF < 1.1) | Electronic | 1 | 59 | 68
F81ILL-R | F96T8 | Fluorescent, (1) 96", T-8 lamp, Instant Start Ballast, RLO (BF < 0.85) | Electronic | 1 | 59 | 57
F81ILL-V | F96T8 | Fluorescent, (1) 96", T-8 lamp, Instant Start Ballast, VHLO (BF > 1.1) | Electronic | 1 | 59 | 71
F81ILU | F96T8 | Flourescent, (1) 96" T-8 lamp, Instant Start Ballast, NLO (0.85 < BF < 0.95) | Prem. Elec. | 1 | 57 | 53
F81LHL/T2 | F96T8/HO | Fluorescent, (1) 96", T-8 HO lamp, Tandem 2-lamp Ballast | Electronic | 1 | 86 | 80
F82IELU | T8F96-57W | Flourescent, (2) 96" T-8 @ 57W lamps, Instant Start Ballast, NLO (0.85 < BF < 0.95) | Prem. Elec. | 2 | 57 | 100
F82ILL | F96T8 | Fluorescent, (2) 96", T-8 lamps, Instant Start Ballast, NLO (0.85 < BF < 0.95) | Electronic | 2 | 59 | 109
F82ILL-R | F96T8 | Fluorescent, (2) 96", T-8 lamps, Instant Start Ballast, RLO (BF < 0.85) | Electronic | 2 | 59 | 98
F82ILL-V | F96T8 | Fluorescent, (2) 96", T-8 lamps, Instant Start Ballast, VHLO (BF > 1.1) | Electronic | 2 | 59 | 149
F82ILU | F96T8 | Flourescent, (2) 96" T-8 ES lamps, Instant Start Ballast, NLO (0.85 < BF < 0.95) | Prem. Elec. | 2 | 59 | 105
F82LHL | F96T8/HO | Fluorescent, (2) 96", T-8 HO lamps | Electronic | 2 | 86 | 160
F83ILL | F96T8 | Fluorescent, (3) 96", T-8 lamps, Instant Start Ballast, NLO (0.85 < BF < 0.95) | Electronic | 3 | 59 | 167
F84ILL | F96T8 | Fluorescent, (4) 96", T-8 lamps, Instant Start Ballast, NLO (0.85 < BF < 0.95) | Electronic | 4 | 59 | 219
F84ILL/2-V | F96T8 | Fluorescent, (4) 96", T-8 lamps, (2) Instant Start Ballasts, VHLO (BF > 1.1) | Electronic | 4 | 59 | 298
F84LHL | F96T8/HO | Fluorescent, (4) 96", T-8 HO lamps | Electronic | 4 | 86 | 320
F86ILL | F96T8 | Fluorescent, (6) 96", T-8 lamps, (2) 3-lamp IS Ballasts, NLO (0.85 < BF < 0.95) | Electronic | 6 | 59 | 327.5
FT5 |  | T5 Linear Fluorescent Systems
F21GPHL-H | F24T5/HO | Fluorescent (1) 22" (563mm) T-5 HO lamp; (1) Prog.Start or PRS Ballast, HLO (.95 < BF < 1.1) | PRS Elec. | 1 | 24 | 27
F21GPL-H | F14T5 | Fluorescent (1) 22" (563mm) T-5 lamp; (1) Prog.Start or PRS Ballast, HLO (.95 < BF < 1.1) | PRS Elec. | 1 | 14 | 18
F22GPHL-H | F24T5/HO | Fluorescent (2) 22" (563mm) T-5 HO lamps; (1) Prog.Start or PRS Ballast, HLO (.95 < BF < 1.1) | PRS Elec. | 2 | 24 | 52
F22GPL-H | F14T5 | Fluorescent (2) 22" (563mm) T-5 lamps; (1) Prog.Start or PRS Ballast, HLO (.95 < BF < 1.1) | PRS Elec. | 2 | 14 | 33
F22PS | F13T5 | Fluorescent, (2) 21", Preheat T5 lamps, (1) Magnetic ballasts with integral starter, (BF=0.80) | Mag-STD | 2 | 13 | 26
F23GPHL/2-H | F24T5/HO | Fluorescent (3) 22" (563mm)T-5 HO lamps; (2) Prog.Start or PRS Ballasts, HLO (.95 < BF < 1.1) | PRS Elec. | 3 | 24 | 79
F23GPL/2-H | F14T5 | Fluorescent (3) 22" (563mm)T-5 lamps; (2) Prog.Start or PRS Ballasts, HLO (.95 < BF < 1.1) | PRS Elec. | 3 | 14 | 51
F23GPL-H | F14T5 | Fluorescent (3) 22" (563mm)T-5 lamps; (1) Prog.Start or PRS Ballast, HLO (.95 < BF < 1.1) | PRS Elec. | 3 | 14 | 50
F24GPHL/2-H | F24T5/HO | Fluorescent (4) 22" (563mm)T-5 HO lamps; (2) Prog.Start or PRS Ballasts, HLO (.95 < BF < 1.1) | PRS Elec. | 4 | 24 | 104
F24GPL/2-H | F14T5 | Fluorescent (4) 22" (563mm)T-5 lamps; (2) Prog.Start or PRS Ballasts, HLO (.95 < BF < 1.1) | PRS Elec. | 4 | 14 | 66
F24PS | F13T5 | Fluorescent, (4) 21", Preheat T5 lamps, (2) Magnetic ballasts with integral starter (BF=0.80) | Mag-STD | 4 | 13 | 53
F31GPHL-H | F39T5/HO | Fluorescent (1) 34" (863mm) T-5 HO lamp; (1) Prog.Start or PRS Ballast, HLO (.95 < BF < 1.1) | PRS Elec. | 1 | 39 | 44
F31GPL-H | F21T5 | Fluorescent (1) 34" (863mm) T-5 lamp; (1) Prog.Start or PRS Ballast, HLO (.95 < BF < 1.1) | PRS Elec. | 1 | 21 | 25
F32GPHL-H | F39T5/HO | Fluorescent (2) 34" (863mm) T-5 HO lamps; (1) Prog.Start or PRS Ballast, HLO (.95 < BF < 1.1) | PRS Elec. | 2 | 39 | 86
F32GPL-H | F21T5 | Fluorescent (2) 34" (863mm) T-5 lamps; (1) Prog.Start or PRS Ballast, HLO (.95 < BF < 1.1) | PRS Elec. | 2 | 21 | 48
F33GPHL/2-H | F39T5/HO | Fluorescent (3) 34" (863mm)T-5 HO lamps; (2) Prog.Start or PRS Ballasts, HLO (.95 < BF < 1.1) | PRS Elec. | 3 | 39 | 130
F33GPL/2-H | F21T5 | Fluorescent (3) 34" (863mm)T-5 lamps; (2) Prog.Start or PRS Ballasts, HLO (.95 < BF < 1.1) | PRS Elec. | 3 | 21 | 73
F34GPHL/2-H | F39T5/HO | Fluorescent (4) 34" (863mm)T-5 HO lamps; (2) Prog.Start or PRS Ballasts, HLO (.95 < BF < 1.1) | PRS Elec. | 4 | 39 | 172
F34GPL/2-H | F21T5 | Fluorescent (4) 34" (863mm)T-5 lamps; (2) Prog.Start or PRS Ballasts, HLO (.95 < BF < 1.1) | PRS Elec. | 4 | 21 | 96
F41GPHL/T2-H | F54T5/HO | Fluorescent (1) T-5 HO 45.8" lamp, Tandem 2-lamp PRS Ballast, HLO (.95 < BF < 1.1) | PRS Elec. | 1 | 54 | 58.5
F41GPHL-H | F54T5/HO | Fluorescent (1) T-5 HO 45.8" lamps, Progammed Rapid Start, Electronic Ballast, HLO (.95 < BF < 1.1) | PRS Elec. | 1 | 54 | 62
F41GPL/T2-H | F28T5 | Fluorescent (1) 45.8" (1163mm) T-5 lamp; Tandem 2-lamp PRS Ballast,HLO (.95 < BF < 1.1) | PRS Elec. | 1 | 28 | 31.5
F41GPL-H | F28T5 | Fluorescent (1) 45.8" (1163mm) T-5 lamp; (1) Prog.Start or PRS Ballast, HLO (.95 < BF < 1.1) | PRS Elec. | 1 | 28 | 33
F42GPHL-H | F54T5/HO | Fluorescent (2) T-5 HO 45.8" lamps, Progammed Rapid Start, Electronic Ballast, HLO (.95 < BF < 1.1) | PRS Elec. | 2 | 54 | 117
F42GPL-H | F28T5 | Fluorescent (2) 45.8" (1163mm) T-5 lamps; (1) Prog.Start or PRS Ballast, HLO (.95 < BF < 1.1) | PRS Elec. | 2 | 28 | 63
F43GPHL/2-H | F54T5/HO | Fluorescent (3) T-5 HO 45.8" lamps, Progammed Rapid Start, (2) Electronic Ballasts, HLO (.95 < BF < 1.1) | PRS Elec. | 3 | 54 | 179
F43GPHL-H | F54T5/HO | Fluorescent, (3) 45.8", T-5 high-output lamps, (1) Programmed Rapid Start Ballast, HLO (.95 < BF < 1.1) | PRS Elec. | 3 | 54 | 179
F43GPL/2-H | F28T5 | Fluorescent (3) 45.8" (1163mm)T-5 lamps; (2) Prog.Start or PRS Ballasts, HLO (.95 < BF < 1.1) | PRS Elec. | 3 | 28 | 96
F44GPHL/2-H | F54T5/HO | Fluorescent (4) T-5 HO 45.8" lamps, Progammed Rapid Start, (2) Electronic Ballasts, HLO (.95 < BF < 1.1) | PRS Elec. | 4 | 54 | 234
F44GPHL-H | F54T5/HO | Fluorescent, (4) 45.8", T-5 high-output lamps, (1) Programmed Rapid Start Ballast, HLO (.95 < BF < 1.1) | PRS Elec. | 4 | 54 | 234
F44GPL/2-H | F28T5 | Fluorescent (4) 45.8" (1163mm)T-5 lamps; (2) Prog.Start or PRS Ballasts, HLO (.95 < BF < 1.1) | PRS Elec. | 4 | 28 | 126
F46GPHL/2-H | F54T5/HO | Fluorescent, (6) 45.8", T-5 high-output lamps, (2) Programmed Rapid Start Ballast, HLO (.95 < BF < 1.1) | PRS Elec. | 6 | 54 | 358
F46GPHL/3-H | F54T5/HO | Fluorescent, (6) 45.8", T-5 high-output lamps, (3) Programmed Rapid Start Ballasts, HLO (.95 < BF < 1.1) | PRS Elec. | 6 | 54 | 351
F48GPHL/2-H | F54T5/HO | Fluorescent, (8) 45.8", T-5 high-output lamps, (2) Programmed Rapid Start Ballasts, HLO (.95 < BF < 1.1) | PRS Elec. | 8 | 54 | 468
F48GPHL/4-H | F54T5/HO | Fluorescent, (8) 45.8", T-5 high-output lamps, (4) Programmed Rapid Start Ballasts, HLO (.95 < BF < 1.1) | PRS Elec. | 8 | 54 | 468
F51GPHL-H | F80T5/HO | Fluorescent (1) 57.6" (1463mm) T-5 HO lamp; (1) Prog.Start or PRS Ballast, HLO (.95 < BF < 1.1) | PRS Elec. | 1 | 80 | 90
F51GPL-H | F35T5 | Fluorescent (1) 57.6" (1463mm) T-5 lamp; (1) Prog.Start or PRS Ballast, HLO (.95 < BF < 1.1) | PRS Elec. | 1 | 35 | 40
F52GPHL/2-H | F80T5/HO | Fluorescent (2) 57.6" (1463mm) T-5 HO lamps; (1) Prog.Start or PRS Ballast, HLO (.95 < BF < 1.1) | PRS Elec. | 2 | 80 | 180
F52GPL-H | F35T5 | Fluorescent (2) 57.6" (1463mm) T-5 lamps; (1) Prog.Start or PRS Ballast, HLO (.95 < BF < 1.1) | PRS Elec. | 2 | 35 | 78
F53GPL/2-H | F35T5 | Fluorescent (3) 57.6" (1463mm)T-5 lamps; (2) Prog.Start or PRS Ballasts, HLO (.95 < BF < 1.1) | PRS Elec. | 3 | 35 | 118
F54GPL/2-H | F35T5 | Fluorescent (4) 57.6" (1463mm)T-5 lamps; (2) Prog.Start or PRS Ballasts, HLO (.95 < BF < 1.1) | PRS Elec. | 4 | 35 | 156
FT12 |  | T12 and Other Linear Fluorescent Systems
F1.51SS | F15T12 | Fluorescent, (1) 18" T12 lamp | Mag-STD | 1 | 15 | 19
F1.52SS | F15T12 | Fluorescent, (2) 18", T12 lamps | Mag-STD | 2 | 15 | 36
F21HS | F24T12/HO | Fluorescent, (1) 24", HO lamp | Mag-STD | 1 | 35 | 62
F21SS | F20T12 | Fluorescent, (1) 24", STD lamp | Mag-STD | 1 | 20 | 25
F22HS | F24T12/HO | Fluorescent, (2) 24", HO lamps | Mag-STD | 2 | 35 | 90
F22SS | F20T12 | Fluorescent, (2) 24", STD lamps | Mag-STD | 2 | 20 | 50
F23SS | F20T12 | Fluorescent, (3) 24", STD lamps | Mag-STD | 3 | 20 | 71
F24SS | F20T12 | Fluorescent, (4) 24", STD lamps | Mag-STD | 4 | 20 | 100
F26SS/2 | F20T12 | Fluorescent, (6) 24", STD lamps, (2) ballasts | Mag-STD | 6 | 20 | 146
F31EE/T2 | F30T12/ES | Fluorescent, (1) 36", ES lamp, Tandem 2-lamp ballast | Mag-ES | 1 | 25 | 33
F31EL | F30T12/ES | Fluorescent, (1) 36", ES lamp | Electronic | 1 | 25 | 26
F31ES | F30T12/ES | Fluorescent, (1) 36", ES lamp | Mag-STD | 1 | 25 | 42
F31ES/T2 | F30T12/ES | Fluorescent, (1) 36", ES lamp, Tandem 2-lamp ballast | Mag-STD | 1 | 25 | 33
F31SE/T2 | F30T12 | Fluorescent, (1) 36", STD lamp, Tandem 2-lamp ballast | Mag-ES | 1 | 30 | 37
F31SHS | F36T12/HO | Fluorescent, (1) 36", HO lamp | Mag-STD | 1 | 50 | 70
F31SL | F30T12 | Fluorescent, (1) 36", STD lamp | Electronic | 1 | 30 | 31
F31SS | F30T12 | Fluorescent, (1) 36", STD lamp | Mag-STD | 1 | 30 | 46
F31SS/T2 | F30T12 | Fluorescent, (1) 36", STD lamp, Tandem 2-lamp ballast | Mag-STD | 1 | 30 | 41
F32EE | F30T12/ES | Fluorescent, (2) 36", ES lamps | Mag-ES | 2 | 25 | 66
F32EL | F30T12/ES | Fluorescent, (2) 36", ES lamps | Electronic | 2 | 25 | 50
F32EL/T4 | F25T12 | Fluorescent, (2) 36" ES lamps, Tandem 4-lamp ballast, NLO (0.85 < BF < 0.95) | Electronic | 2 | 25 | 50
F32ES | F30T12/ES | Fluorescent, (2) 36", ES lamps | Mag-STD | 2 | 25 | 73
F32SE | F30T12 | Fluorescent, (2) 36", STD lamps | Mag-ES | 2 | 30 | 74
F32SHS | F36T12/HO | Fluorescent, (2) 36", HO, lamps | Mag-STD | 2 | 50 | 114
F32SL | F30T12 | Fluorescent, (2) 36", STD lamps | Electronic | 2 | 30 | 58
F32SS | F30T12 | Fluorescent, (2) 36", STD lamps | Mag-STD | 2 | 30 | 75
F33ES | F30T12/ES | Fluorescent, (3) 36", ES lamps | Mag-STD | 3 | 25 | 115
F33SE | F30T12 | Fluorescent, (3) 36", STD lamps, (1) STD ballast and (1) ES ballast | Mag-ES | 3 | 30 | 120
F33SS | F30T12 | Fluorescent, (3) 36", STD lamps | Mag-STD | 3 | 30 | 127
F34EE | F30T12/ES | Fluorescent, (4) 36", ES lamps | Mag-ES | 4 | 25 | 132
F34SE | F30T12 | Fluorescent, (4) 36", STD lamps | Mag-ES | 4 | 30 | 148
F34SL | F30T12 | Fluorescent, (4) 36", STD lamps | Electronic | 4 | 30 | 116
F34SS | F30T12 | Fluorescent, (4) 36", STD lamps | Mag-STD | 4 | 30 | 150
F36EE | F30T12/ES | Fluorescent, (6) 36", ES lamps | Mag-ES | 6 | 30 | 198
F36ES | F30T12/ES | Fluorescent, (6) 36", ES lamps | Mag-STD | 6 | 30 | 219
F36SE | F30T12 | Fluorescent, (6) 36", STD lamps | Mag-ES | 6 | 30 | 213
F36SS | F30T12 | Fluorescent, (6) 36", STD lamps | Mag-STD | 6 | 30 | 225
F40SE/D1 | None | Fluorescent, (0) 48" lamps, Completely delamped fixture with (1) hot ballast | Mag-ES | 1 | 0 | 4
F40SE/D2 | None | Fluorescent, (0) 48" lamps, Completely delamped fixture with (2) hot ballast | Mag-ES | 1 | 0 | 8
F41EE | F40T12/ES | Fluorescent, (1) 48", ES lamp | Mag-ES | 1 | 34 | 43
F41EE/D2 | F40T12/ES | Fluorescent, (1) 48", ES lamp, 2 ballast | Mag-ES | 1 | 34 | 43
F41EE/T2 | F40T12/ES | Fluorescent, (1) 48", ES lamp, Tandem 2-lamp ballast | Mag-ES | 1 | 34 | 36
F41EHS | F48T12/HO/ES | Fluorescent, (1) 48", ES HO lamp | Mag-STD | 1 | 55 | 80
F41EIS | F48T12/ES | Fluorescent, (1) 48" ES Instant Start lamp. Magnetic ballast | Mag-STD | 1 | 30 | 51
F41EL | F40T12/ES | Fluorescent, (1) 48", T12 ES lamp, Electronic Ballast | Electronic | 1 | 34 | 32
F41IAL | F25T12 | Fluorescent, (1) 48", F25T12 lamp, Instant Start Ballast | Electronic | 1 | 25 | 25
F41IAL/T2-R | F25T18 | Fluorescent, (1) 48", F25T12 lamp, Tandem 2-Lamp IS ballast, RLO (BF < 0.85) | Electronic | 1 | 25 | 19
F41IAL/T3-R | F25T17 | Fluorescent, (1) 48", F25T12 lamp, Tandem 3-Lamp IS ballast, RLO (BF < 0.85) | Electronic | 1 | 25 | 20
F41IAL/T4-R | F25T17 | Fluorescent, (1) 48", F25T12 lamp, Tandem 4-Lamp IS ballast, RLO (BF < 0.85) | Electronic | 1 | 25 | 20
F41SHS | F48T12/HO | Fluorescent, (1) 48", STD HO lamp | Mag-STD | 1 | 60 | 85
F41SIL | F40T12 | Fluorescent, (1) 48", STD IS lamp, Electronic ballast | Electronic | 1 | 39 | 46
F41SIL/T2 | F40T12 | Fluorescent, (1) 48", STD IS lamp, Tandem 2-lamp IS ballast | Electronic | 1 | 39 | 37
F41SVS | F48T12/VHO | Fluorescent, (1) 48", STD VHO lamp | Mag-STD | 1 | 110 | 140
F41TS | F40T10 | Fluorescent, (1) 48", T-10 lamp | Mag-STD | 1 | 40 | 51
F42EE | F40T12/ES | Fluorescent, (2) 48", ES lamp | Mag-ES | 2 | 34 | 72
F42EE/2 | F40T12/ES | Fluorescent, (2) 48", ES lamps, (2) 1-lamp ballasts | Mag-ES | 2 | 34 | 86
F42EE/D2 | F40T12/ES | Fluorescent, (2) 48", ES lamps, 2 Ballasts (delamped) | Mag-ES | 2 | 34 | 76
F42EHS | F42T12/HO/ES | Fluorescent, (2) 42", HO lamps (3.5' lamp) | Mag-STD | 2 | 55 | 135
F42EIS | F48T12/ES | Fluorescent, (2) 48" ES Instant Start lamps. Magnetic ballast | Mag-STD | 2 | 30 | 82
F42EL | F40T12/ES | Fluorescent, (2) 48", T12 ES lamps, Electronic Ballast | Electronic | 2 | 34 | 60
F42IAL/T4-R | F25T12 | Fluorescent, (2) 48", F25T12 lamps, Tandem 4-lamp IS Ballast, RLO (BF < 0.85) | Electronic | 2 | 25 | 40
F42IAL-R | F25T12 | Fluorescent, (2) 48", F25T12 lamps, Instant Start Ballast, RLO (BF < 0.85) | Electronic | 2 | 25 | 39
F42SHS | F48T12/HO | Fluorescent, (2) 48", STD HO lamps | Mag-STD | 2 | 60 | 145
F42SIL | F40T12 | Fluorescent, (2) 48", STD IS lamps, Electronic ballast | Electronic | 2 | 39 | 74
F42SVS | F48T12/VHO | Fluorescent, (2) 48", STD VHO lamps | Mag-STD | 2 | 110 | 252
F43EE | F40T12/ES | Fluorescent, (3) 48", ES lamps | Mag-ES | 3 | 34 | 115
F43EE/T2 | F40T12/ES | Fluorescent, (3) 48", ES lamps, Tandem 2-lamp ballasts | Mag-ES | 3 | 34 | 108
F43EHS | F42T12/HO/ES | Fluorescent, (3) 42", HO lamps (3.5' lamp) | Mag-STD | 3 | 55 | 215
F43EIS | F48T12/ES | Fluorescent, (3) 48" ES Instant Start lamps. Magnetic ballast | Mag-STD | 3 | 30 | 133
F43EL | F40T12/ES | Fluorescent, (3) 48", T12 ES lamps, Electronic Ballast | Electronic | 3 | 34 | 92
F43IAL-R | F25T12 | Fluorescent, (3) 48", F25T12 lamps, Instant Start Ballast, RLO (BF < 0.85) | Electronic | 3 | 25 | 60
F43SHS | F48T12/HO | Fluorescent, (3) 48", STD HO lamps | Mag-STD | 3 | 60 | 230
F43SIL | F40T12 | Fluorescent, (3) 48", STD IS lamps, Electronic ballast | Electronic | 3 | 39 | 120
F43SVS | F48T12/VHO | Fluorescent, (3) 48", STD VHO lamps | Mag-STD | 3 | 110 | 377
F44EE | F40T12/ES | Fluorescent, (4) 48", ES lamps | Mag-ES | 4 | 34 | 144
F44EE/D3 | F40T12/ES | Fluorescent, (4) 48", ES lamps, 3 Ballasts (delamped) | Mag-ES | 4 | 34 | 148
F44EE/D4 | F40T12/ES | Fluorescent, (4) 48", ES lamps, 4 Ballasts (delamped) | Mag-ES | 4 | 34 | 152
F44EHS | F48T12/HO/ES | Fluorescent, (4) 48", ES HO lamps | Mag-STD | 4 | 55 | 270
F44EIS | F48T12/ES | Fluorescent, (4) 48" ES Instant Start lamps. Magnetic ballast | Mag-STD | 4 | 30 | 164
F44EL | F40T12/ES | Fluorescent, (4) 48", T12 ES lamps, Electronic Ballast | Electronic | 4 | 34 | 120
F44EVS | F48T12/VHO/ES | Fluorescent, (4) 48", VHO ES lamps | Mag-STD | 4 | 0 | 420
F44IAL-R | F25T12 | Fluorescent, (4) 48", F25T12 lamps, Instant Start Ballast, RLO (BF < 0.85) | Electronic | 4 | 25 | 80
F44SHS | F48T12/HO | Fluorescent, (4) 48", STD HO lamps | Mag-STD | 4 | 60 | 290
F44SIL | F40T12 | Fluorescent, (4) 48", STD IS lamps, Electronic ballast | Electronic | 4 | 39 | 148
F44SVS | F48T12/VHO | Fluorescent, (4) 48", STD VHO lamps | Mag-STD | 4 | 110 | 484
F46EE | F40T12/ES | Fluorescent, (6) 48", ES lamps | Mag-ES | 6 | 34 | 216
F46EL | F40T12/ES | Fluorescent, (6) 48", ES lamps | Electronic | 6 | 34 | 180
F46SL | F40T12 | Fluorescent, (6) 48", STD lamps | Electronic | 6 | 40 | 186
F48EE | F40T12/ES | Fluorescent, (8) 48", ES lamps | Mag-ES | 8 | 34 | 288
F51SHE | F60T12/HO | Fluorescent, (1) 60", STD HO lamp | Mag-ES | 1 | 75 | 88
F51SHL | F60T12/HO | Fluorescent, (1) 60", STD HO lamp | Electronic | 1 | 75 | 69
F51SHS | F60T12/HO | Fluorescent, (1) 60", STD HO lamp | Mag-STD | 1 | 75 | 92
F51SL | F60T12 | Fluorescent, (1) 60", STD lamp | Electronic | 1 | 50 | 44
F51SS | F60T12 | Fluorescent, (1) 60", STD lamp | Mag-STD | 1 | 50 | 63
F51SVS | F60T12/VHO | Fluorescent, (1) 60", VHO ES lamp | Mag-STD | 1 | 135 | 165
F52SHE | F60T12/HO | Fluorescent, (2) 60", STD HO lamps | Mag-ES | 2 | 75 | 176
F52SHL | F60T12/HO | Fluorescent, (2) 60", STD HO lamps | Electronic | 2 | 75 | 138
F52SHS | F60T12/HO | Fluorescent, (2) 60", STD HO lamps | Mag-STD | 2 | 75 | 168
F52SL | F60T12 | Fluorescent, (2) 60", STD lamps | Electronic | 2 | 50 | 88
F52SS | F60T12 | Fluorescent, (2) 60", STD lamps | Mag-STD | 2 | 50 | 128
F52SVS | F60T12/VHO | Fluorescent, (2) 60", VHO ES lamps | Mag-STD | 2 | 135 | 310
F61ISL | F72T12 | Fluorescent, (1) 72", STD lamp, IS electronic ballast | Electronic | 1 | 55 | 68
F61SHS | F72T12/HO | Fluorescent, (1) 72", STD HO lamp | Mag-STD | 1 | 85 | 106
F61SS | F72T12 | Fluorescent, (1) 72", STD lamp | Mag-STD | 1 | 55 | 76
F61SVS | F72T12/VHO | Fluorescent, (1) 72", VHO lamp | Mag-STD | 1 | 160 | 180
F62ISL | F72T12 | Fluorescent, (2) 72", STD lamps, IS electronic ballast | Electronic | 2 | 55 | 108
F62SE | F72T12 | Fluorescent, (2) 72", STD lamps | Mag-ES | 2 | 55 | 122
F62SHE | F72T12/HO | Fluorescent, (2) 72", STD HO lamps | Mag-ES | 2 | 85 | 194
F62SHL | F72T12/HO | Fluorescent, (2) 72", STD HO lamps | Electronic | 2 | 85 | 167
F62SHS | F72T12/HO | Fluorescent, (2) 72", STD HO lamps | Mag-STD | 2 | 85 | 200
F62SL | F72T12 | Fluorescent, (2) 72", STD lamps | Electronic | 2 | 55 | 108
F62SS | F72T12 | Fluorescent, (2) 72", STD lamps | Mag-STD | 2 | 55 | 142
F62SVS | F72T12/VHO | Fluorescent, (2) 72", VHO lamps | Mag-STD | 2 | 160 | 330
F63ISL | F72T12 | Fluorescent, (3) 72", STD lamps, IS electronic ballast | Electronic | 3 | 55 | 176
F63SS | F72T12 | Fluorescent, (3) 72", STD lamps | Mag-STD | 3 | 55 | 202
F64ISL | F72T12 | Fluorescent, (4) 72", STD lamps, IS electronic ballast | Electronic | 4 | 55 | 216
F64SE | F72T12 | Fluorescent, (4) 72", STD lamps | Mag-ES | 4 | 55 | 244
F64SHE | F72T12/HO | Fluorescent, (4) 72", HO lamps | Mag-ES | 4 | 85 | 388
F64SS | F72T12 | Fluorescent, (4) 72", STD lamps | Mag-STD | 4 | 56 | 244
F81EE | F96T12/ES | Fluorescent, (1) 96" ES lamp | Mag-ES | 1 | 60 | 75
F81EE/T2 | F96T12/ES | Fluorescent, (1) 96", ES lamp, Tandem 2-lamp ballst | Mag-ES | 1 | 60 | 61.5
F81EHL | F96T12/HO/ES | Fluorescent, (1) 96", ES HO lamp | Electronic | 1 | 95 | 80
F81EHS | F96T12/HO/ES | Fluorescent, (1) 96", ES HO lamp | Mag-STD | 1 | 95 | 113
F81EL | F96T12/ES | Fluorescent, (1) 96", ES lamp | Electronic | 1 | 60 | 69
F81EL/T2 | F96T12/ES | Fluorescent, (1) 96", ES lamp, Tandem 2-lamp ballast | Electronic | 1 | 60 | 55
F81EVS | F96T12/VHO/ES | Fluorescent, (1) 96", ES VHO lamp | Mag-STD | 1 | 185 | 205
F81SGS | F96T17 | Fluorescent, (1) 96", T17 Grooved lamp | Mag-STD | 1 | 215 | 235
F81SHS | F96T12/HO | Fluorescent, (1) 96", STD HO lamp | Mag-STD | 1 | 110 | 121
F81SL | F96T12 | Fluorescent, (1) 96", STD lamp | Electronic | 1 | 75 | 69
F81SL/T2 | F96T12 | Fluorescent, (1) 96", STD lamp, Tandem 2-lamp ballast | Electronic | 1 | 75 | 55
F81SVS | F96T12/VHO | Fluorescent, (1) 96", STD VHO lamp | Mag-STD | 1 | 215 | 205
F82EE | F96T12/ES | Fluorescent, (2) 96", ES lamps | Mag-ES | 2 | 60 | 123
F82EHE | F96T12/HO/ES | Fluorescent, (2) 96", ES HO lamps | Mag-ES | 2 | 95 | 207
F82EHL | F96T12/HO/ES | Fluorescent, (2) 96", ES HO lamps | Electronic | 2 | 95 | 173
F82EHS | F96T12/HO/ES | Fluorescent, (2) 96", ES HO lamps | Mag-STD | 2 | 95 | 207
F82EL | F96T12/ES | Fluorescent, (2) 96", ES lamps | Electronic | 2 | 60 | 110
F82EVS | F96T12/VHO/ES | Fluorescent, (2) 96", ES VHO lamps | Mag-STD | 2 | 195 | 390
F82SHE | F96T12/HO | Fluorescent, (2) 96", STD HO lamps | Mag-ES | 2 | 110 | 207
F82SHL | F96T12/HO | Fluorescent, (2) 96", STD HO lamps | Electronic | 2 | 110 | 173
F82SHS | F96T12/HO | Fluorescent, (2) 96", STD HO lamps | Mag-STD | 2 | 110 | 207
F82SL | F96T12 | Fluorescent, (2) 96", STD lamps | Electronic | 2 | 75 | 110
F82SVS | F96T12/VHO | Fluorescent, (2) 96", STD VHO lamps | Mag-STD | 2 | 215 | 380
F83EE | F96T12/ES | Fluorescent, (3) 96", ES lamps | Mag-ES | 3 | 60 | 198
F83EHE | F96T12/HO/ES | Fluorescent, (3) 96", ES HO lamps, (1) 2-lamp ES Ballast and (1) 1-lamp STD Ballast | Mag-ES/STD | 3 | 95 | 319
F83EHS | F96T12/HO/ES | Fluorescent, (3) 96", ES HO lamps | Mag-STD | 3 | 95 | 319
F83EL | F96T12/ES | Fluorescent, (3) 96", ES lamps | Electronic | 3 | 60 | 179
F83EVS | F96T12/VHO/ES | Fluorescent, (3) 96", ES VHO lamps | Mag-STD | 3 | 185 | 585
F83SHE | F96T12/HO | Fluorescent, (3) 96", STD HO lamps | Mag-ES | 3 | 110 | 319
F83SHS | F96T12/HO | Fluorescent, (3) 96", STD HO lamps | Mag-STD | 3 | 110 | 319
F83SL | F96T12 | Fluorescent, (3) 96", STD lamps | Electronic | 3 | 75 | 179
F83SVS | F96T12/VHO | Fluorescent, (3) 96", STD VHO lamps | Mag-STD | 3 | 215 | 585
F84EE | F96T12/ES | Fluorescent, (4) 96", ES lamps | Mag-ES | 4 | 60 | 246
F84EHE | F96T12/HO/ES | Fluorescent, (4) 96", ES HO lamps | Mag-ES | 4 | 95 | 414
F84EHL | F96T12/HO/ES | Fluorescent, (4) 96", ES HO lamps | Electronic | 4 | 95 | 346
F84EHS | F96T12/HO/ES | Fluorescent, (4) 96", ES HO lamps | Mag-STD | 4 | 95 | 414
F84EL | F96T12/ES | Fluorescent, (4) 96", ES lamps | Electronic | 4 | 60 | 220
F84EVS | F96T12/VHO/ES | Fluorescent, (4) 96", ES VHO lamps | Mag-STD | 4 | 185 | 760
F84SHE | F96T12/HO | Fluorescent, (4) 96", STD HO lamps | Mag-ES | 4 | 110 | 414
F84SHL | F96T12/HO | Fluorescent, (4) 96", STD HO lamps | Electronic | 4 | 110 | 346
F84SHS | F96T12/HO | Fluorescent, (4) 96", STD HO lamps | Mag-STD | 4 | 110 | 414
F84SL | F96T12 | Fluorescent, (4) 96", STD lamps | Electronic | 4 | 75 | 220
F84SVS | F96T12/VHO | Fluorescent, (4) 96", STD VHO lamps | Mag-STD | 4 | 215 | 760
F86EE | F96T12/ES | Fluorescent, (6) 96", ES lamps | Mag-ES | 6 | 60 | 369
F86EHS | F96T12/HO/ES | Fluorescent, (6) 96", ES HO lamps | Mag-STD | 6 | 95 | 519
F88EHE | F96T12/HO/ES | Fluorescent, (8) 96", ES HO lamps | Mag-ES | 8 | 95 | 828
F88SHS | F96T12/HO | Fluorescent, (8) 96", STD HO lamps | Mag-STD | 8 | 110 | 828
FC |  | Circline Fluorescent Fixtures
FC12/1 | FC12T9 | Fluorescent, (1) 12" circular lamp, RS ballast | Mag-STD | 1 | 32 | 31
FC12/2 | FC12T9 | Fluorescent, (2) 12" circular lamps, RS ballast | Mag-STD | 2 | 32 | 62
FC16/1 | FC16T9 | Fluorescent, (1) 16" circular lamp | Mag-STD | 1 | 40 | 35
FC20 | FC6T9 | Fluorescent, Circline, (1) 20W lamp, preheat ballast | Mag-STD | 1 | 20 | 20
FC22 | FC8T9 | Fluorescent, Circline, (1) 22W lamp, preheat ballast | Mag-STD | 1 | 22 | 20
FC32 | FC12T9 | Fluorescent, Circline, (1) 32W lamp, preheat ballast | Mag-STD | 1 | 32 | 40
FC40 | FC16T9 | Fluorescent, Circline, (1) 32W lamp, preheat ballast | Mag-STD | 1 | 32 | 42
FC6/1 | FC6T9 | Fluorescent, (1) 6" circular lamp, RS ballast | Mag-STD | 1 | 20 | 25
FC8/1 | FC8T9 | Fluorescent, (1) 8" circular lamp, RS ballast | Mag-STD | 1 | 22 | 26
FC8/2 | FC8T9 | Fluorescent, (2) 8" circular lamps, RS ballast | Mag-STD | 2 | 22 | 52
FU |  | U-Tube Fluorescent Fixtures
FU1EE | FU40T12/ES | Fluorescent, (1) U-Tube, ES lamp | Mag-ES | 1 | 35 | 43
FU1ES | FU40T12/ES | Fluorescent, (1) U-Tube, ES Lamp | Mag-STD | 1 | 34 | 43
FU1ILL | FU31T8/6 | Fluorescent, (1) U-Tube, T-8 lamp, Instant Start ballast | Electronic | 1 | 32 | 31
FU1ILU | FU32T8/6 | Fluorescent, (1) 6" spacing U-Tube, T-8 lamp, IS Ballast, NLO (0.85 < BF < 0.95) | Prem. Elec. | 1 | 32 | 29
FU1ILU-H | FU32T8/6 | Fluorescent, (1) 6" spacing U-Tube, T-8 lamp, IS Ballast, HLO (.95 < BF < 1.1) | Prem. Elec. | 1 | 32 | 34
FU1LL | FU31T8/6 | Fluorescent, (1) U-Tube, T-8 lamp | Electronic | 1 | 32 | 32
FU1LL-R | FU31T8/6 | Fluorescent, (1) U-Tube, T-8 lamp, RLO (BF < 0.85) | Electronic | 1 | 31 | 27
FU1SE | FU40T12 | Fluorescent, (1) U-Tube, STD lamp | Mag-ES | 1 | 40 | 43
FU1SS | FU40T12 | Fluorescent, (1) U-Tube, ES Lamp | Mag-STD | 1 | 40 | 43
FU2EE | FU40T12/ES | Fluorescent, (2) U-Tube, ES lamps | Mag-ES | 2 | 35 | 72
FU2EL | FU40T12/ES | Fluorescent (2) 48" U-bent ES lamps, Electronic ballast, NLO (0.85 < BF < 0.95) | Electronic | 2 | 34 | 63
FU2ES | FU40T12/ES | Fluorescent, (2) U-Tube, ES lamps | Mag-STD | 1 | 35 | 72
FU2ILL | FU31T8/6 | Fluorescent, (2) U-Tube, T-8 lamps, Instand Start Ballast | Electronic | 2 | 32 | 59
FU2ILL/T4 | FU31T8/6 | Fluorescent, (2) U-Tube, T-8 lamps, Instand Start Ballast, Tandem 4-lamp ballast | Electronic | 2 | 32 | 56
FU2ILL/T4-R | FU31T8/6 | Fluorescent, (2) U-Tube, T-8 lamps, Instand Start Ballast, RLO, Tandem 4-lamp ballast | Electronic | 2 | 32 | 49
FU2ILL-H | FU31T8/6 | Fluorescent, (2) U-Tube, T-8 lamps, Instand Start HLO Ballast | Electronic | 2 | 32 | 65
FU2ILL-R | FU31T8/6 | Fluorescent, (2) U-Tube, T-8 lamps, Instand Start RLO Ballast | Electronic | 2 | 32 | 52
FU2ILU | FU32T8/6 | Fluorescent, (2) 6" spacing U-Tube, T-8 lamps, IS Ballast, NLO (0.85 < BF < 0.95) | Prem. Elec. | 2 | 32 | 55
FU2ILU-R | FU32T8/6 | Fluorescent, (2) 6" spacing U-Tube, T-8 lamps, IS Ballast, RLO (BF < 0.85) | Prem. Elec. | 2 | 32 | 48
FU2LL | FU31T8/6 | Fluorescent, (2) U-Tube, T-8 lamps | Electronic | 2 | 32 | 60
FU2LL/T2 | FU31T8/6 | Fluorescent, (2) U-Tube, T-8 lamps, Tandem 4-lamp ballast | Electronic | 2 | 32 | 59
FU2LL-R | FU31T8/6 | Fluorescent, (2) U-Tube, T-8 lamps, RLO (BF < 0.85) | Electronic | 2 | 31 | 54
FU2SE | FU40T12 | Fluorescent, (2) U-Tube, STD lamps | Mag-ES | 2 | 40 | 72
FU2SL | FU40T12 | Fluorescent (2) 48" U-bent Standard lamps, Electronic ballast, NLO (0.85 < BF < 0.95) | Electronic | 2 | 40 | 63
FU2SS | FU40T12 | Fluorescent, (1) U-Tube, STD lamp, STD Mag Ballast | Mag-STD | 2 | 40 | 72
FU3EE | FU40T12/ES | Fluorescent, (3) U-Tube, ES lamps | Mag-ES | 3 | 35 | 115
FU3ILL | FU31T8/6 | Fluorescent, (3) U-Tube, T-8 lamps, Instand Start Ballast | Electronic | 3 | 32 | 89
FU3ILL-R | FU31T8/6 | Fluorescent, (3) U-Tube, T-8 lamps, Instand Start RLO Ballast | Electronic | 3 | 32 | 78
FU3ILU | FU32T8/6 | Fluorescent, (3) 6" spacing U-Tube, T-8 lamps, IS Ballast, NLO (0.85 < BF < 0.95) | Prem. Elec. | 3 | 32 | 81
FU3ILU-R | FU32T8/6 | Fluorescent, (3) 6" spacing U-Tube, T-8 lamps, IS Ballast, RLO (BF < 0.85) | Prem. Elec. | 3 | 32 | 73
FU3SE | FU40T12 | Fluorescent, (3) U-Tube, STD lamps | Mag-ES | 3 | 40 | 115
H |  | Halogen Incandescent Fixtures
H100/1 | H100 | Halogen Incandescent, (1) 100W lamp |  | 1 | 100 | 100
H150/1 | H150 | Halogen Incandescent, (1) 150W lamp |  | 1 | 150 | 150
H250/1 | H250 | Halogen Incandescent, (1) 250W lamp |  | 1 | 250 | 250
H300/1 | H300 | Halogen Incandescent, (1) 300W lamp |  | 1 | 300 | 300
H35/1 | H35 | Halogen Incandescent, (1) 35W lamp |  | 1 | 35 | 35
H42/1 | H42 | Halogen Incandescent, (1) 42W lamp |  | 1 | 42 | 42
H45/1 | H45 | Halogen Incandescent, (1) 45W lamp |  | 1 | 45 | 45
H50/1 | H50 | Halogen Incandescent, (1) 50W lamp |  | 1 | 50 | 50
H500/1 | H500 | Halogen Incandescent, (1) 500W lamp |  | 1 | 500 | 500
H52/1 | H52 | Halogen Incandescent, (1) 52W lamp |  | 1 | 52 | 52
H55/1 | H55 | Halogen Incandescent, (1) 55W lamp |  | 1 | 55 | 55
H60/1 | H60 | Halogen Incandescent, (1) 60W lamp |  | 1 | 60 | 60
H72/1 | H72 | Halogen Incandescent, (1) 72W lamp |  | 1 | 72 | 72
H75/1 | H75 | Halogen Incandescent, (1) 75W lamp |  | 1 | 75 | 75
H90/1 | H90 | Halogen Incandescent, (1) 90W lamp |  | 1 | 90 | 90
HLV50/1 | H50/LV | Halogen, (1) Low Voltage MR16 lamp |  | 1 | 50 | 60
HPS |  | High Pressure Sodium Fixtures
HPS100/1 | HPS100 | High Pressure Sodium, (1) 100W lamp |  | 1 | 100 | 138
HPS1000/1 | HPS1000 | High Pressure Sodium, (1) 1000W lamp |  | 1 | 1000 | 1100
HPS150/1 | HPS150 | High Pressure Sodium, (1) 150W lamp |  | 1 | 150 | 188
HPS200/1 | HPS200 | High Pressure Sodium, (1) 200W lamp |  | 1 | 200 | 250
HPS250/1 | HPS250 | High Pressure Sodium, (1) 250W lamp |  | 1 | 250 | 295
HPS310/1 | HPS310 | High Pressure Sodium, (1) 310W lamp |  | 1 | 310 | 365
HPS35/1 | HPS35 | High Pressure Sodium, (1) 35W lamp |  | 1 | 35 | 46
HPS360/1 | HPS360 | High Pressure Sodium, (1) 360W lamp |  | 1 | 360 | 414
HPS400/1 | HPS400 | High Pressure Sodium, (1) 400W lamp |  | 1 | 400 | 465
HPS50/1 | HPS50 | High Pressure Sodium, (1) 50W lamp |  | 1 | 50 | 66
HPS70/1 | HPS70 | High Pressure Sodium, (1) 70W lamp |  | 1 | 70 | 95
I |  | Standard Incandescent Fixtures
I100/1 | I100 | Incandescent, (1) 100W lamp |  | 1 | 100 | 100
I1000/1 | I1000 | Incandescent, (1) 1000W lamp |  | 1 | 1000 | 1000
I100E/1 | I100/ES | Incandescent, (1) 100W ES lamp |  | 1 | 90 | 90
I100EL/1 | I100/ES/LL | Incandescent, (1) 100W ES/LL lamp |  | 1 | 90 | 90
I110/1 | I110 | Incandescent, (1) 110W lamp |  | 1 | 110 | 110
I116/1 | I116 | Incandescent, (1) 116W lamp |  | 1 | 116 | 116
I120/1 | I120 | Incandescent, (1) 120W lamp |  | 1 | 120 | 120
I120/1 | I120 | Incandescent, (1) 120W lamp |  | 1 | 120 | 120
I125/1 | I125 | Incandescent, (1) 125W lamp |  | 1 | 125 | 125
I130/1 | I130 | Incandescent, (1) 130W lamp |  | 1 | 130 | 130
I135/1 | I135 | Incandescent, (1) 135W lamp |  | 1 | 135 | 135
I15/1 | I15 | Incandescent, (1) 15W lamp |  | 1 | 15 | 15
I150/1 | I150 | Incandescent, (1) 150W lamp |  | 1 | 150 | 150
I1500/1 | I1500 | Incandescent, (1) 1500W lamp |  | 1 | 1500 | 1500
I150E/1 | I150/ES | Incandescent, (1) 150W ES lamp |  | 1 | 135 | 135
I150EL/1 | I150/ES/LL | Incandescent, (1) 150W ES/LL lamp |  | 1 | 135 | 135
I160/1 | I160 | Incandescent, (1) 160W lamp |  | 1 | 160 | 160
I170/1 | I170 | Incandescent, (1) 170W lamp |  | 1 | 170 | 170
I20/1 | I20 | Incandescent, (1) 20W lamp |  | 1 | 20 | 20
I200/1 | I200 | Incandescent, (1) 200W lamp |  | 1 | 200 | 200
I2000/1 | I2000 | Incandescent, (1) 2000W lamp |  | 1 | 2000 | 2000
I200L/1 | I200/LL | Incandescent, (1) 200W LL lamp |  | 1 | 200 | 200
I25/1 | I25 | Incandescent, (1) 25W lamp |  | 1 | 25 | 25
I250/1 | I250 | Incandescent, (1) 250W lamp |  | 1 | 250 | 250
I30/1 | I30 | Incandescent, (1) 30W lamp |  | 1 | 30 | 30
I300/1 | I300 | Incandescent, (1) 300W lamp |  | 1 | 300 | 300
I34/1 | I34 | Incandescent, (1) 34W lamp |  | 1 | 34 | 34
I36/1 | I36 | Incandescent, (1) 36W lamp |  | 1 | 36 | 36
I40/1 | I40 | Incandescent, (1) 40W lamp |  | 1 | 40 | 40
I400/1 | I400 | Incandescent, (1) 400W lamp |  | 1 | 400 | 400
I40E/1 | I40/ES | Incandescent, (1) 40W ES lamp |  | 1 | 34 | 34
I40EL/1 | I40/ES/LL | Incandescent, (1) 40W ES/LL lamp |  | 1 | 34 | 34
I42/1 | I42 | Incandescent, (1) 42W lamp |  | 1 | 42 | 42
I448/1 | I448 | Incandescent, (1) 448W lamp |  | 1 | 448 | 448
I45/1 | I45 | Incandescent, (1) 45W lamp |  | 1 | 45 | 45
I50/1 | I50 | Incandescent, (1) 50W lamp |  | 1 | 50 | 50
I500/1 | I500 | Incandescent, (1) 500W lamp |  | 1 | 500 | 500
I52/1 | I52 | Incandescent, (1) 52W lamp |  | 1 | 52 | 52
I54/1 | I54 | Incandescent, (1) 54W lamp |  | 1 | 54 | 54
I55/1 | I55 | Incandescent, (1) 55W lamp |  | 1 | 55 | 55
I60/1 | I60 | Incandescent, (1) 60W lamp |  | 1 | 60 | 60
I60E/1 | I60/ES | Incandescent, (1) 60W ES lamp |  | 1 | 52 | 52
I60EL/1 | I60/ES/LL | Incandescent, (1) 60W ES/LL lamp |  | 1 | 52 | 52
I65/1 | I65 | Incandescent, (1) 65W lamp |  | 1 | 65 | 65
I65/1 | I65 | Incandescent, (1) 65W lamp |  | 1 | 65 | 65
I67/1 | I67 | Incandescent, (1) 67W lamp |  | 1 | 67 | 67
I69/1 | I69 | Incandescent, (1) 69W lamp |  | 1 | 69 | 69
I7.5/1 | I7.5 | Tungsten exit light, (1) 7.5 W lamp, used in night light application |  | 1 | 7.5 | 8
I72/1 | I72 | Incandescent, (1) 72W lamp |  | 1 | 72 | 72
I75/1 | I75 | Incandescent, (1) 75W lamp |  | 1 | 75 | 75
I750/1 | I750 | Incandescent, (1) 750W lamp |  | 1 | 750 | 750
I75E/1 | I75/ES | Incandescent, (1) 75W ES lamp |  | 1 | 67 | 67
I75EL/1 | I75/ES/LL | Incandescent, (1) 75W ES/LL lamp |  | 1 | 67 | 67
I80/1 | I80 | Incandescent, (1) 80W lamp |  | 1 | 80 | 80
I85/1 | I85 | Incandescent, (1) 85W lamp |  | 1 | 85 | 85
I90/1 | I90 | Incandescent, (1) 90W lamp |  | 1 | 90 | 90
I93/1 | I93 | Incandescent, (1) 93W lamp |  | 1 | 93 | 93
I95/1 | I95 | Incandescent, (1) 95W lamp |  | 1 | 95 | 95
LED |  | LED Traffic Signal Fixtures
LED12GA | LED 12" Green Arrow | LED Traffic Signal Light, 12" Green Arrow |  | 1 | 8 | 8
LED12GB | LED 12" Green Ball | LED Traffic Signal Light, 12" Green Ball |  | 1 | 12 | 12
LED12RA | LED 12" Red Arrow | LED Traffic Signal Light, 12" Red Arrow |  | 1 | 7 | 7
LED12RB | LED 12" Red Ball | LED Traffic Signal Light, 12" Red Ball |  | 1 | 10 | 10
LED12YA | LED 12" Yellow Arrow | LED Traffic Signal Light, 12" Yellow Arrow |  | 1 | 9 | 9
LED12YB | LED 12" Yellow Ball | LED Traffic Signal Light, 12" Yellow Ball |  | 1 | 17 | 17
LED8GB | LED 8" Green Ball | LED Traffic Signal Light, 8" Green Ball |  | 1 | 8 | 8
LED8RB | LED 8" Red Ball | LED Traffic Signal Light, 8" Red Ball |  | 1 | 6 | 6
LED8YB | LED 8" Yellow Ball | LED Traffic Signal Light, 8" Yellow Ball |  | 1 | 12 | 12
LEDPCOUNT | Countdown Led | LED, P(edestrian), COUNT(down timer) (Side by Side or dedicated fixture) |  | 1 | 7 | 7
LEDPH12OF | Overlay Filled Hand | LED, P(edestrian), H(and), in 12" x 12" enclosure, O(verlay), F(illed) |  | 1 | 8 | 8
LEDPH12OO | Overlay Outline Hand | LED, P(edestrian), H(and), in 12" x 12" enclosure, O(verlay), O(utline) |  | 1 | 6 | 6
LEDPH12F | Filled Hand Only | LED, P(edestrian), H(and), 12" x 12" enclosure, H(and) Only, F(illed) |  | 1 | 7 | 7
LEDPH12O | Outline Hand Only | LED, P(edestrian), H(and), 12" x 12" enclosure, H(and) Only, O(utline) |  | 1 | 6 | 6
LEDPH12SF | Side by Side Filled Hand | LED, P(edestrian), H(and), one half of 12" x 12" enclosure, S(ide by Side), F(illed) |  | 1 | 7 | 7
LEDPH16OF | Overlay Filled Hand | LED P(edestrian), H(and), in 16" x 18" enclosure, O(verlay), F(illed) |  | 1 | 9 | 9
LEDPH16OO | Overlay Outline Hand | LED P(edestrian), H(and), in 16" x 18" enclosure, O(verlay), O(utline) |  | 1 | 8 | 8
LEDPH16SF | Side by Side Filled Hand | LED P(edestrian), H(and), one half of 16" x 18" enclosure, S(ide by side), F(illed) |  | 1 | 11 | 11
LEDPH16SO | Side by Side Outline Hand | LED P(edestrian), H(and), one half of 16" x 18" enclosure, S(ide by side), O(utline) |  | 1 | 6 | 6
LEDPP12OF | Overlay Filled Person | LED, P(edestrian), P(erson), in 12" x 12" enclosure, O(verlay), F(illed) |  | 1 | 7 | 7
LEDPP12OO | Overlay Outline Person | LED, P(edestrian), P(erson), 12" x 12" enclosure, O(verlay), O(utline) |  | 1 | 6 | 6
LEDPP12F | Filled Person Only | LED, P(edestrian), P(erson), 12" x 12" enclosure, P(erson) Only, F(illed) |  | 1 | 7 | 7
LEDPP12O | Outline Person Only | LED, P(edestrian), P(erson), 12" x 12" enclosure, P(erson) Only, O(utline) |  | 1 | 5 | 5
LEDPP12SO | Side by Side Outline Person | LED, P(edestrian), P(erson), one half of 12" x 12" enclosure, S(ide by Side), O(utline) |  | 1 | 4 | 4
LEDPP16OF | Overlay Filled Person | LED, P(edestrian), P(erson), in 16" x 18" Enclosure, O(verlay), F(illed) |  | 1 | 8 | 8
LEDPP16OO | Overlay Outline Person | LED, P(edestrian), P(erson), in 16" x 18" Enclosure, O(verlay), O(utline) |  | 1 | 8 | 8
LEDPP16SF | Side by Side Filled Person | LED, P(edestrian), P(erson), one half of 16" x 18" enclosure, S(ide by side), F(illed) |  | 1 | 8 | 8
LEDPP16SO | Side by Side Outline Person | LED, P(edestrian), P(erson), one half of 16" x 18" enclosure, S(ide by side), O(utline) |  | 1 | 7 | 7
LEDO |  | LED Fixtures - Other
LEDO37C | 5mm LED W | LED Canopy Fixture, Small |  | 1 | 37 | 37
LEDO50C | 5mm LED W | LED Canopy Fixture, Large |  | 1 | 50 | 50
LEDO37WP | 5mm LED W | LED Wall Pack, Small |  | 1 | 37 | 37
LEDO50WP | 5mm LED W | LED Wall Pack, Large |  | 1 | 50 | 50
MH |  | Metal Halide Fixtures
MH100/1 | MH100 | Metal Halide, (1) 100W lamp, Magnetic ballast | Magnetic | 1 | 100 | 127
MH100/1-L | MH100 | Metal Halide, (1) 100W lamp, Electronic ballast | Electronic | 1 | 100 | 111
MH1000/1 | MH1000 | Metal Halide, (1) 1000W lamp, Magnetic ballast | Magnetic | 1 | 1000 | 1077
MH125/1 | MH125 | Metal Halide, (1) 125W lamp, Magnetic ballast | Magnetic | 1 | 125 | 150
MH150/1 | MH150 | Metal Halide, (1) 150W lamp, Magnetic ballast | Magnetic | 1 | 150 | 184
MH150/1-L | MH150 | Metal Halide, (1) 150W lamp, Electronic ballast | Electronic | 1 | 150 | 167
MH1500/1 | MH1500 | Metal Halide, (1) 1500W lamp, Magnetic ballast | Magnetic | 1 | 1500 | 1608
MH175/1 | MH175 | Metal Halide, (1) 175W lamp, Magnetic ballast | Magnetic | 1 | 175 | 209
MH175/1-L | MH175 | Metal Halide, (1) 175W lamp, Electronic ballast | Electronic | 1 | 175 | 191
MH200/1 | MH200 | Metal Halide, (1) 200W lamp, Magnetic ballast | Magnetic | 1 | 200 | 232
MH200/1-L | MH200 | Metal Halide, (1) 200W lamp, Electronic ballast | Magnetic | 1 | 200 | 219
MH250/1 | MH250 | Metal Halide, (1) 250W lamp, Magnetic ballast | Magnetic | 1 | 250 | 291
MH32/1 | MH32 | Metal Halide, (1) 32W lamp, Magnetic ballast | Magnetic | 1 | 32 | 42
MH320/1 | MH320 | Metal Halide, (1) 320W lamp, Magnetic ballast | Magnetic | 1 | 320 | 367
MH350/1 | MH350 | Metal Halide, (1) 350W lamp, Magnetic ballast | Magnetic | 1 | 350 | 395
MH360/1 | MH360 | Metal Halide, (1) 360W lamp, Magnetic ballast | Magnetic | 1 | 360 | 418
MH39/1 | MH39 | Metal Halide, (1) 39W lamp, Magnetic ballast | Magnetic | 1 | 39 | 56
MH39/1-L | MH39 | Metal Halide, (1) 39W lamp, Electronic ballast | Electronic | 1 | 39 | 44
MH400/1 | MH400 | Metal Halide, (1) 400W lamp, Magnetic ballast | Magnetic | 1 | 400 | 456
MH450/1 | MH450 | Metal Halide, (1) 450W lamp, Magnetic ballast | Magnetic | 1 | 450 | 507
MH50/1 | MH50 | Metal Halide, (1) 50W lamp, Magnetic ballast | Magnetic | 1 | 50 | 67
MH50/1-L | MH50 | Metal Halide, (1) 50W lamp, Electronic ballast | Electronic | 1 | 50 | 57
MH70/1 | MH70 | Metal Halide, (1) 70W lamp, Magnetic ballast | Magnetic | 1 | 70 | 94
MH70/1-L | MH70 | Metal Halide, (1) 70W lamp, Electronic ballast | Electronic | 1 | 70 | 79
MH750/1 | MH750 | Metal Halide, (1) 750W lamp, Magnetic ballast | Magnetic | 1 | 750 | 814
MV |  | Mercury Vapor Fixtures
MV100/1 | MV100 | Mercury Vapor, (1) 100W lamp |  | 1 | 100 | 125
MV1000/1 | MV1000 | Mercury Vapor, (1) 1000W lamp |  | 1 | 1000 | 1075
MV160/1 | MV160-SB | Mercury Vapor, Self-Ballasted, (1) 160W self-ballasted lamp |  | 1 | 160 | 160
MV175/1 | MV175 | Mercury Vapor, (1) 175W lamp |  | 1 | 175 | 205
MV250/1 | MV250 | Mercury Vapor, (1) 250W lamp |  | 1 | 250 | 290
MV40/1 | MV40 | Mercury Vapor, (1) 40W lamp |  | 1 | 40 | 50
MV400/1 | MV400 | Mercury Vapor, (1) 400W lamp |  | 1 | 400 | 455
MV50/1 | MV50 | Mercury Vapor, (1) 50W lamp |  | 1 | 50 | 74
MV700/1 | MV700 | Mercury Vapor, (1) 700W lamp |  | 1 | 700 | 780
MV75/1 | MV75 | Mercury Vapor, (1) 75W lamp |  | 1 | 75 | 93
NEON |  | NEON Fixtures
NEONEPH | Neon | NEON E(lectonic ballast) P(edestrian) H(and) |  | 1 | 26 | 26
NEONEPP | Neon | NEON E(lectonic ballast) P(edestrian) P(erson) |  | 1 | 26 | 26
NEONMPDW | Neon | NEON M(agnetic tranformer) P(edestrian) D(on't)W(alk) |  | 1 | 81 | 81
NEONMPH | Neon | NEON M(agnetic tranformer) P(edestrian) H(and) |  | 1 | 45 | 45
NEONMPP | Neon | NEON M(agnetic tranformer) P(edestrian) P(erson) |  | 1 | 38 | 38
REMOVED |  | Removed Fixtures
Removed | None | Fixture completely removed from service |  | 0 | 0 | 0

## Wattage Lookup (hidden)
SORTED by |  | Regulation
FIXTURE | LAMP | WATT/
CODE | CODE | FIXT
CF
CF11/1-SCRW | CF11W | 11
CF13/1-SCRW | CF13W | 13
CF14/1-SCRW | CF14W | 14
CF15/1-SCRW | CF15W | 15
CF16/1-SCRW | CF16W | 16
CF17/1-SCRW | CF17W | 17
CF18/1-SCRW | CF18W | 18
CF2/1-SCRW | CF2W | 2
CF20/1-SCRW | CF20W | 20
CF23/1-SCRW | CF23W | 23
CF25/1-SCRW | CF25W | 25
CF26/1-SCRW | CF26W | 26
CF27/1-SCRW | CF27W | 27
CF28/1-SCRW | CF28W | 28
CF32/1-SCRW | CF32W | 32
CF4/1-SCRW | CF4W | 4
CF42/1-SCRW | CF42W | 42
CF44/1-SCRW | CF44W | 44
CF7/1-SCRW | CF7W | 7
CF9/1-SCRW | CF9W | 9
CFD10/1 | CFD10W | 16
CFD16/1 | CFD16W | 26
CFD21/1 | CFD21W | 26
CFD28/1 | CFD28W | 35
CFD38/1 | CFD38W | 46
CFM13/1-L | CFM13W | 16
CFM13/2-L | CFM13W | 30
CFM18/1-L | CFM18W | 20
CFM18/2-L | CFM18W | 40
CFM26/1-L | CFM26W | 29
CFM26/2-L | CFM26W | 51
CFM32/1-L | CFM32W | 35
CFM42/1-L | CFM42W | 48
CFM42/2-L | CFM42W | 93
CFM42/8-L | CFM42W | 372
CFQ10/1 | CFQ10W | 15
CFQ13/1 | CFQ13W | 17
CFQ13/1-L | CFQ13W | 15
CFQ13/2 | CFQ13W | 31
CFQ13/2-L | CFQ13W | 28
CFQ13/3 | CFQ13W | 48
CFQ15/1 | CFQ15W | 20
CFQ17/1 | CFQ17W | 24
CFQ17/2 | CFQ17W | 48
CFQ18/1 | CFQ18W | 26
CFQ18/1-L | CFQ18W | 20
CFQ18/2 | CFQ18W | 45
CFQ18/2-L | CFQ18W | 38
CFQ18/4 | CFQ18W | 90
CFQ20/1 | CFQ20W | 23
CFQ20/2 | CFQ20W | 46
CFQ22/1 | CFQ22W | 24
CFQ22/2 | CFQ22W | 48
CFQ22/3 | CFQ22W | 72
CFQ23/1 | CFQ23W | 27
CFQ25/1 | CFQ25W | 33
CFQ25/2 | CFQ25W | 66
CFQ26/1 | CFQ26W | 33
CFQ26/1-L | CFQ26W | 27
CFQ26/2 | CFQ26W | 66
CFQ26/2-L | CFQ26W | 50
CFQ26/3 | CFQ26W | 99
CFQ26/6-L | CFQ26W | 150
CFQ28/1 | CFQ28W | 33
CFQ28/1-L | CFQ28W | 31
CFQ28/2-L | CFQ28W | 60
CFQ9/1 | CFQ9W | 14
CFQ9/2 | CFQ9W | 23
CFT13/1 | CFT13W | 17
CFT13/1-L | CFT13W | 15
CFT13/2 | CFT13W | 31
CFT13/2-L | CFT13W | 28
CFT13/3 | CFT13W | 48
CFT18/1 | CFT18W | 24
CFT18/1-L | CFT18W | 20
CFT18/2 | CFT18W | 38
CFT22/1 | CFT22W | 27
CFT22/2 | CFT22W | 54
CFT22/4 | CFT22W | 108
CFT24/1 | CFT24W | 32
CFT26/1 | CFT26W | 32
CFT26/1-L | CFT26W | 27
CFT26/2-L | CFT26W | 51
CFT28/1 | CFT28W | 33
CFT28/2 | CFT28W | 66
CFT32/1-L | CFM32W | 34
CFT32/2-L | CFM32W | 62
CFT32/6-L | CFM32W | 186
CFT36/1 | CFT36W | 51
CFT40/1 | CFT40W | 46
CFT40/1-L | CFT40W | 43
CFT40/2 | CFT40W | 85
CFT40/2-L | CFT40W | 72
CFT40/3 | CFT40W | 133
CFT40/3-L | CFT40W | 105
CFT5/1 | CFT5W | 9
CFT5/2 | CFT5W | 18
CFT55/1-L | CFT55W | 60
CFT55/2-L | CFT55W | 110
CFT55/3-L | CFT55W | 170
CFT55/4-L | CFT55W | 220
CFT7/1 | CFT7W | 10
CFT7/2 | CFT7W | 21
CFT9/1 | CFT9W | 12
CFT9/2 | CFT9W | 23
CFT9/3 | CFT9W | 34
ECF
ECF5/1 | CFT5W | 9
ECF5/2 | CFT5W | 20
ECF6/1 | CFT6W | 13
ECF6/2 | CFT6W | 26
ECF7/1 | CFT7W | 10
ECF7/2 | CFT7W | 21
ECF9/1 | CFT9W | 12
ECF9/2 | CFT9W | 20
EF2/2 | F2T1 | 5
EF6/1 | F6T5 | 9
EF6/2 | F6T5 | 18
EF8/1 | F8T5 | 12
EF8/2 | F8T5 | 24
EI10/2 | I10 | 20
EI15/1 | I15 | 15
EI15/2 | I15 | 30
EI20/1 | I20 | 20
EI20/2 | I20 | 40
EI25/1 | I25 | 25
EI25/2 | I25 | 50
EI34/1 | I34 | 34
EI34/2 | I34 | 68
EI40/1 | I40 | 40
EI40/2 | I40 | 80
EI5/1 | I5 | 5
EI5/2 | I5 | 10
EI50/2 | I50 | 100
EI6/1 | 6S6 | 6
EI6/2 | 6S6 | 12
EI7.5/1 | I7.5 | 8
EI7.5/2 | I7.5 | 15
ELED2/1 | LED2W | 6
ELED2/2 | LED2W | 9
ELED3 | LED3W | 3
F
FT8
F1.51LS | F15T8 | 19
F1.52LS | F15T8 | 36
F21ILL | F17T8 | 18
F21ILL/T2 | F17T8 | 16.5
F21ILL/T2-R | F17T8 | 15
F21ILL/T3 | F17T8 | 15.6667
F21ILL/T3-R | F17T8 | 13.6667
F21ILL/T4 | F17T8 | 14.75
F21ILL/T4-R | F17T8 | 13.25
F21ILL-R | F17T8 | 17
F21ILU | F17T8 | 17
F21ILU-R | F17T8 | 15
F21LL | F17T8 | 16
F21LL/T2 | F17T8 | 15.5
F21LL/T3 | F17T8 | 17.3333
F21LL/T4 | F17T8 | 17
F21LL-R | F17T8 | 15
F21SL | F17T8 | 24
F22ILL | F17T8 | 33
F22ILL/T4 | F17T8 | 29.5
F22ILL/T4-R | F17T8 | 26.5
F22ILL-R | F17T8 | 30
F22ILU | F17T8 | 30
F22ILU-R | F17T8 | 27
F22LL | F17T8 | 31
F22LL/T4 | F17T8 | 34
F22LL-R | F17T8 | 28
F23ILL | F17T8 | 47
F23ILL-H | F17T8 | 51
F23ILL-R | F17T8 | 41
F23ILU | F17T8 | 45
F23ILU-R | F17T8 | 40
F23LL | F17T8 | 52
F23LL-R | F17T8 | 41
F24ILL | F17T8 | 59
F24ILL-R | F17T8 | 53
F24ILU | F17T8 | 57
F24ILU-R | F17T8 | 52
F24LL | F17T8 | 68
F24LL-R | F17T8 | 57
F31ILL | F25T8 | 26
F31ILL/T2 | F25T8 | 23
F31ILL/T2-H | F25T8 | 26
F31ILL/T2-R | F25T8 | 21
F31ILL/T3 | F25T8 | 22.6667
F31ILL/T3-R | F25T8 | 20.3333
F31ILL/T4 | F25T8 | 22
F31ILL/T4-R | F25T8 | 19.5
F31ILL-H | F25T8 | 28
F31ILL-R | F25T8 | 22
F31ILU | F25T8 | 23
F31ILU/T2 | F25T8 | 22
F31ILU/T2-R | F25T8 | 19.5
F31ILU/T3-R | F25T8 | 19.3333
F31ILU/T4-R | F25T8 | 19.25
F31ILU-R | F25T8 | 20
F31LL | F25T8 | 24
F31LL/T2 | F25T8 | 23
F31LL/T3 | F25T8 | 24
F31LL/T4 | F25T8 | 22.25
F31LL-H | F25T8 | 26
F31LL-R | F25T8 | 23
F32ILL | F25T8 | 46
F32ILL/2-R | F25T8 | 44
F32ILL/T4 | F25T8 | 44
F32ILL/T4-R | F25T8 | 39
F32ILL-H | F25T8 | 52
F32ILL-R | F25T8 | 42
F32ILU | F25T8 | 44
F32ILU/T4-R | F25T8 | 38.5
F32ILU-R | F25T8 | 39
F32LL | F25T8 | 46
F32LL/T4 | F25T8 | 44.5
F32LL-H | F25T8 | 50
F32LL-R | F25T8 | 42
F32LL-V | F25T8 | 70
F33ILL | F25T8 | 68
F33ILL-R | F25T8 | 61
F33ILU | F25T8 | 65
F33ILU-R | F25T8 | 58
F33LL | F25T8 | 72
F33LL-R | F25T8 | 62
F34ILL | F25T8 | 88
F34ILL/2-R | F25T8 | 84
F34ILL-R | F25T8 | 78
F34ILU | F25T8 | 86
F34ILU-R | F25T8 | 77
F34LL | F25T8 | 89
F34LL-R | F25T8 | 84
F36ILL/2 | F25T8 | 135
F36ILL/2-R | F25T8 | 121
F41GELL | F32T8-30W | 28
F41GELL-R | F32T8-30W | 24
F41GLL | F32T8 | 30
F41GLL-R | F32T8 | 25
F41GRLL | F28T8-28W | 26
F41GRLL-R | F28T8-28W | 22
F41IELL | F32T8-30W | 29
F41IELL/T2 | F32T8-30W | 27.5
F41IELL/T3 | F32T8-30W | 27
F41IELL/T4 | F32T8-30W | 26.5
F41IELL-H | F32T8-30W | 34
F41IELL-R | F32T8-30W | 26
F41IELU | F32T8-30W | 27
F41IELU/T2 | F32T8-30W | 26
F41IELU/T2-R | F32T8-30W | 22.5
F41IELU/T3 | F32T8-30W | 25.6667
F41IELU/T3-R | F32T8-30W | 22.6667
F41IELU/T4 | F32T8-30W | 25.25
F41IELU/T4-R | F32T8-30W | 22.25
F41IELU-H | F32T8-30W | 32
F41IELU-R | F32T8-30W | 24
F41ILL | F32T8 | 31
F41ILL/T2 | F32T8 | 29
F41ILL/T2-H | F32T8 | 33
F41ILL/T2-R | F32T8 | 25.5
F41ILL/T3 | F32T8 | 28.3333
F41ILL/T3-H | F32T8 | 31
F41ILL/T3-R | F32T8 | 25.3333
F41ILL/T4 | F32T8 | 28
F41ILL/T4-R | F32T8 | 24.5
F41ILL-H | F32T8 | 36
F41ILL-R | F32T8 | 27
F41ILU | F32T8 | 28
F41ILU/T2 | F32T8 | 27
F41ILU/T2-R | F32T8 | 24
F41ILU/T3 | F32T8 | 27
F41ILU/T3-R | F32T8 | 24
F41ILU/T4 | F32T8 | 26.75
F41ILU/T4-R | F32T8 | 23.75
F41ILU-H | F32T8 | 35
F41ILU-R | F32T8 | 25
F41IRLL | F28T8-28W | 27
F41IRLL-V | F28T8-28W | 35
F41IRLU | F28T8-28W | 25
F41IRLU-R | F28T8-28W | 22
F41LE | F32T8 | 35
F41LHL | F48T8/HO | 59
F41LL | F32T8 | 32
F41LL/T2 | F32T8 | 30
F41LL/T2-H | F32T8 | 35
F41LL/T2-R | F32T8 | 27
F41LL/T3 | F32T8 | 31
F41LL/T3-H | F32T8 | 32.6667
F41LL/T3-R | F32T8 | 25.3333
F41LL/T4 | F32T8 | 29.5
F41LL/T4-R | F32T8 | 26.25
F41LL-H | F32T8 | 39
F41LL-R | F32T8 | 27
F42GELL | F32T8-30W | 56
F42GELL-R | F32T8-30W | 43
F42GLL | F32T8 | 59
F42GLL-R | F32T8 | 47
F42GRLL | F28T8-28W | 49
F42GRLL-R | F28T8-28W | 40
F42IELL | F32T8-30W | 55
F42IELL/T4 | F32T8-30W | 53
F42IELL/T4-R | F32T8-30W | 46
F42IELL-H | F32T8-30W | 62
F42IELL-R | F32T8-30W | 49
F42IELU | F32T8-30W | 52
F42IELU/T4 | F32T8-30W | 50.5
F42IELU/T4-R | F32T8-30W | 44.5
F42IELU-R | F32T8-30W | 45
F42ILL | F32T8 | 58
F42ILL/2 | F32T8 | 62
F42ILL/2-R | F32T8 | 54
F42ILL/T4 | F32T8 | 56
F42ILL/T4-R | F32T8 | 49
F42ILL-H | F32T8 | 66
F42ILL-R | F32T8 | 51
F42ILL-V | F32T8 | 77
F42ILU | F32T8 | 54
F42ILU/T4 | F32T8 | 53.5
F42ILU/T4-R | F32T8 | 47.5
F42ILU-R | F32T8 | 48
F42IRLL | F28T8-28W | 52
F42IRLL-V | F28T8-28W | 68
F42IRLU | F28T8-28W | 48
F42IRLU-R | F28T8-28W | 43
F42IRLU-V | F28T8-28W | 65
F42LE | F32T8 | 71
F42LHL | F48T8/HO | 98
F42LL | F32T8 | 60
F42LL/2 | F32T8 | 64
F42LL/T4 | F32T8 | 59
F42LL/T4-R | F32T8 | 52.5
F42LL-H | F32T8 | 70
F42LL-R | F32T8 | 54
F42LL-V | F32T8 | 85
F43GELL | F32T8-30W | 83
F43GELL-R | F32T8-30W | 67
F43GLL | F32T8 | 88
F43GLL-R | F32T8 | 72
F43GRLL | F28T8-28W | 75
F43GRLL-R | F28T8-28W | 62
F43IELL | F32T8-30W | 81
F43IELL/2 | F32T8-30W | 84
F43IELL/2-H | F32T8-30W | 96
F43IELL/2-R | F32T8-30W | 75
F43IELL-H | F32T8-30W | 86
F43IELL-R | F32T8-30W | 71
F43IELU | F32T8-30W | 77
F43IELU-R | F32T8-30W | 68
F43ILL | F32T8 | 85
F43ILL/2 | F32T8 | 89
F43ILL/2-H | F32T8 | 102
F43ILL/2-R | F32T8 | 78
F43ILL-H | F32T8 | 93
F43ILL-R | F32T8 | 76
F43ILL-V | F32T8 | 112
F43ILU | F32T8 | 81
F43ILU-R | F32T8 | 72
F43IRLL | F28T8-28W | 76
F43IRLL-H | F28T8-28W | 82
F43IRLL-V | F28T8-28W | 97
F43IRLU | F28T8-28W | 72
F43IRLU-R | F28T8-28W | 63
F43IRLU-V | F28T8-28W | 96
F43LE | F32T8 | 110
F43LHL | F48T8/HO | 157
F43LL | F32T8 | 93
F43LL/2 | F32T8 | 92
F43LL-H | F32T8 | 98
F43LL-R | F32T8 | 76
F44GELL | F32T8-30W | 109
F44GELL-R | F32T8-30W | 86
F44GLL | F32T8 | 115
F44GLL-R | F32T8 | 92
F44GRLL | F28T8-28W | 99
F44GRLL-R | F28T8-28W | 80
F44IELL | F32T8-30W | 106
F44IELL/2 | F32T8-30W | 110
F44IELL/2-H | F32T8-30W | 124
F44IELL/2-R | F32T8-30W | 98
F44IELL-R | F32T8-30W | 92
F44IELU | F32T8-30W | 101
F44IELU-R | F32T8-30W | 89
F44ILL | F32T8 | 112
F44ILL/2 | F32T8 | 116
F44ILL/2-H | F32T8 | 132
F44ILL/2-R | F32T8 | 102
F44ILL/2-V | F32T8 | 154
F44ILL-R | F32T8 | 98
F44ILL-V | F32T8 | 151
F44ILU | F32T8 | 107
F44ILU-R | F32T8 | 95
F44IRLL | F28T8-28W | 99
F44IRLL-R | F28T8-28W | 85
F44IRLU | F28T8-28W | 94
F44IRLU-R | F28T8-28W | 83
F44IRLU-V | F28T8-28W | 131
F44LE | F32T8 | 142
F44LHL | F48T8/HO | 196
F44LL | F32T8 | 118
F44LL/2 | F32T8 | 120
F44LL-R | F32T8 | 105
F45ILL/2 | F32T8 | 143
F46GLL/2-R | F32T8 | 141.5
F46IELU/2 | F32T8-30W | 153.5
F46IELU/2-R | F32T8-30W | 135
F46ILL/2 | F32T8 | 170
F46ILL/2-R | F32T8 | 150.5
F46ILL/2-V | F32T8 | 226
F46ILU/2 | F32T8 | 161.5
F46ILU/2-R | F32T8 | 143.5
F46IRLU/2-R | F28T8-28W | 126
F46LL/2 | F32T8 | 182
F48ILL/2 | F32T8 | 224
F48ILL/2-R | F32T8 | 196
F51ILL | F40T8 | 36
F51ILL/T2 | F40T8 | 36
F51ILL/T3 | F40T8 | 35.3333
F51ILL/T4 | F40T8 | 33.5
F51ILL-R | F40T8 | 43
F52ILL | F40T8 | 72
F52ILL/T4 | F40T8 | 67
F52ILL-H | F40T8 | 80
F52ILL-R | F40T8 | 73
F53ILL | F40T8 | 106
F53ILL-H | F40T8 | 108
F54ILL | F40T8 | 134
F54ILL-H | F40T8 | 126
F81IELU | F96T8-57W | 51
F81ILL | F96T8 | 58
F81ILL/T2 | F96T8 | 54.5
F81ILL/T2-R | F96T8 | 49
F81ILL-H | F96T8 | 68
F81ILL-R | F96T8 | 57
F81ILL-V | F96T8 | 71
F81ILU | F96T8 | 53
F81LHL/T2 | F96T8/HO | 80
F82IELU | T8F96-57W | 100
F82ILL | F96T8 | 109
F82ILL-R | F96T8 | 98
F82ILL-V | F96T8 | 149
F82ILU | F96T8 | 105
F82LHL | F96T8/HO | 160
F83ILL | F96T8 | 167
F84ILL | F96T8 | 219
F84ILL/2-V | F96T8 | 298
F84LHL | F96T8/HO | 320
F86ILL | F96T8 | 327.5
FT5
F21GPHL-H | F24T5/HO | 27
F21GPL-H | F14T5 | 18
F22GPHL-H | F24T5/HO | 52
F22GPL-H | F14T5 | 33
F22PS | F13T5 | 26
F23GPHL/2-H | F24T5/HO | 79
F23GPL/2-H | F14T5 | 51
F23GPL-H | F14T5 | 50
F24GPHL/2-H | F24T5/HO | 104
F24GPL/2-H | F14T5 | 66
F24PS | F13T5 | 53
F31GPHL-H | F39T5/HO | 44
F31GPL-H | F21T5 | 25
F32GPHL-H | F39T5/HO | 86
F32GPL-H | F21T5 | 48
F33GPHL/2-H | F39T5/HO | 130
F33GPL/2-H | F21T5 | 73
F34GPHL/2-H | F39T5/HO | 172
F34GPL/2-H | F21T5 | 96
F41GPHL/T2-H | F54T5/HO | 58.5
F41GPHL-H | F54T5/HO | 62
F41GPL/T2-H | F28T5 | 31.5
F41GPL-H | F28T5 | 33
F42GPHL-H | F54T5/HO | 117
F42GPL-H | F28T5 | 63
F43GPHL/2-H | F54T5/HO | 179
F43GPHL-H | F54T5/HO | 179
F43GPL/2-H | F28T5 | 96
F44GPHL/2-H | F54T5/HO | 234
F44GPHL-H | F54T5/HO | 234
F44GPL/2-H | F28T5 | 126
F46GPHL/2-H | F54T5/HO | 358
F46GPHL/3-H | F54T5/HO | 351
F48GPHL/2-H | F54T5/HO | 468
F48GPHL/4-H | F54T5/HO | 468
F51GPHL-H | F80T5/HO | 90
F51GPL-H | F35T5 | 40
F52GPHL/2-H | F80T5/HO | 180
F52GPL-H | F35T5 | 78
F53GPL/2-H | F35T5 | 118
F54GPL/2-H | F35T5 | 156
FT12
F1.51SS | F15T12 | 19
F1.52SS | F15T12 | 36
F21HS | F24T12/HO | 62
F21SS | F20T12 | 25
F22HS | F24T12/HO | 90
F22SS | F20T12 | 50
F23SS | F20T12 | 71
F24SS | F20T12 | 100
F26SS/2 | F20T12 | 146
F31EE/T2 | F30T12/ES | 33
F31EL | F30T12/ES | 26
F31ES | F30T12/ES | 42
F31ES/T2 | F30T12/ES | 33
F31SE/T2 | F30T12 | 37
F31SHS | F36T12/HO | 70
F31SL | F30T12 | 31
F31SS | F30T12 | 46
F31SS/T2 | F30T12 | 41
F32EE | F30T12/ES | 66
F32EL | F30T12/ES | 50
F32EL/T4 | F25T12 | 50
F32ES | F30T12/ES | 73
F32SE | F30T12 | 74
F32SHS | F36T12/HO | 114
F32SL | F30T12 | 58
F32SS | F30T12 | 75
F33ES | F30T12/ES | 115
F33SE | F30T12 | 120
F33SS | F30T12 | 127
F34EE | F30T12/ES | 132
F34SE | F30T12 | 148
F34SL | F30T12 | 116
F34SS | F30T12 | 150
F36EE | F30T12/ES | 198
F36ES | F30T12/ES | 219
F36SE | F30T12 | 213
F36SS | F30T12 | 225
F40SE/D1 | None | 4
F40SE/D2 | None | 8
F41EE | F40T12/ES | 43
F41EE/D2 | F40T12/ES | 43
F41EE/T2 | F40T12/ES | 36
F41EHS | F48T12/HO/ES | 80
F41EIS | F48T12/ES | 51
F41EL | F40T12/ES | 32
F41IAL | F25T12 | 25
F41IAL/T2-R | F25T18 | 19
F41IAL/T3-R | F25T17 | 20
F41IAL/T4-R | F25T17 | 20
F41SHS | F48T12/HO | 85
F41SIL | F40T12 | 46
F41SIL/T2 | F40T12 | 37
F41SVS | F48T12/VHO | 140
F41TS | F40T10 | 51
F42EE | F40T12/ES | 72
F42EE/2 | F40T12/ES | 86
F42EE/D2 | F40T12/ES | 76
F42EHS | F42T12/HO/ES | 135
F42EIS | F48T12/ES | 82
F42EL | F40T12/ES | 60
F42IAL/T4-R | F25T12 | 40
F42IAL-R | F25T12 | 39
F42SHS | F48T12/HO | 145
F42SIL | F40T12 | 74
F42SVS | F48T12/VHO | 252
F43EE | F40T12/ES | 115
F43EE/T2 | F40T12/ES | 108
F43EHS | F42T12/HO/ES | 215
F43EIS | F48T12/ES | 133
F43EL | F40T12/ES | 92
F43IAL-R | F25T12 | 60
F43SHS | F48T12/HO | 230
F43SIL | F40T12 | 120
F43SVS | F48T12/VHO | 377
F44EE | F40T12/ES | 144
F44EE/D3 | F40T12/ES | 148
F44EE/D4 | F40T12/ES | 152
F44EHS | F48T12/HO/ES | 270
F44EIS | F48T12/ES | 164
F44EL | F40T12/ES | 120
F44EVS | F48T12/VHO/ES | 420
F44IAL-R | F25T12 | 80
F44SHS | F48T12/HO | 290
F44SIL | F40T12 | 148
F44SVS | F48T12/VHO | 484
F46EE | F40T12/ES | 216
F46EL | F40T12/ES | 180
F46SL | F40T12 | 186
F48EE | F40T12/ES | 288
F51SHE | F60T12/HO | 88
F51SHL | F60T12/HO | 69
F51SHS | F60T12/HO | 92
F51SL | F60T12 | 44
F51SS | F60T12 | 63
F51SVS | F60T12/VHO | 165
F52SHE | F60T12/HO | 176
F52SHL | F60T12/HO | 138
F52SHS | F60T12/HO | 168
F52SL | F60T12 | 88
F52SS | F60T12 | 128
F52SVS | F60T12/VHO | 310
F61ISL | F72T12 | 68
F61SHS | F72T12/HO | 106
F61SS | F72T12 | 76
F61SVS | F72T12/VHO | 180
F62ISL | F72T12 | 108
F62SE | F72T12 | 122
F62SHE | F72T12/HO | 194
F62SHL | F72T12/HO | 167
F62SHS | F72T12/HO | 200
F62SL | F72T12 | 108
F62SS | F72T12 | 142
F62SVS | F72T12/VHO | 330
F63ISL | F72T12 | 176
F63SS | F72T12 | 202
F64ISL | F72T12 | 216
F64SE | F72T12 | 244
F64SHE | F72T12/HO | 388
F64SS | F72T12 | 244
F81EE | F96T12/ES | 75
F81EE/T2 | F96T12/ES | 61.5
F81EHL | F96T12/HO/ES | 80
F81EHS | F96T12/HO/ES | 113
F81EL | F96T12/ES | 69
F81EL/T2 | F96T12/ES | 55
F81EVS | F96T12/VHO/ES | 205
F81SGS | F96T17 | 235
F81SHS | F96T12/HO | 121
F81SL | F96T12 | 69
F81SL/T2 | F96T12 | 55
F81SVS | F96T12/VHO | 205
F82EE | F96T12/ES | 123
F82EHE | F96T12/HO/ES | 207
F82EHL | F96T12/HO/ES | 173
F82EHS | F96T12/HO/ES | 207
F82EL | F96T12/ES | 110
F82EVS | F96T12/VHO/ES | 390
F82SHE | F96T12/HO | 207
F82SHL | F96T12/HO | 173
F82SHS | F96T12/HO | 207
F82SL | F96T12 | 110
F82SVS | F96T12/VHO | 380
F83EE | F96T12/ES | 198
F83EHE | F96T12/HO/ES | 319
F83EHS | F96T12/HO/ES | 319
F83EL | F96T12/ES | 179
F83EVS | F96T12/VHO/ES | 585
F83SHE | F96T12/HO | 319
F83SHS | F96T12/HO | 319
F83SL | F96T12 | 179
F83SVS | F96T12/VHO | 585
F84EE | F96T12/ES | 246
F84EHE | F96T12/HO/ES | 414
F84EHL | F96T12/HO/ES | 346
F84EHS | F96T12/HO/ES | 414
F84EL | F96T12/ES | 220
F84EVS | F96T12/VHO/ES | 760
F84SHE | F96T12/HO | 414
F84SHL | F96T12/HO | 346
F84SHS | F96T12/HO | 414
F84SL | F96T12 | 220
F84SVS | F96T12/VHO | 760
F86EE | F96T12/ES | 369
F86EHS | F96T12/HO/ES | 519
F88EHE | F96T12/HO/ES | 828
F88SHS | F96T12/HO | 828
FC
FC12/1 | FC12T9 | 31
FC12/2 | FC12T9 | 62
FC16/1 | FC16T9 | 35
FC20 | FC6T9 | 20
FC22 | FC8T9 | 20
FC32 | FC12T9 | 40
FC40 | FC16T9 | 42
FC6/1 | FC6T9 | 25
FC8/1 | FC8T9 | 26
FC8/2 | FC8T9 | 52
FU
FU1EE | FU40T12/ES | 43
FU1ES | FU40T12/ES | 43
FU1ILL | FU31T8/6 | 31
FU1ILU | FU32T8/6 | 29
FU1ILU-H | FU32T8/6 | 34
FU1LL | FU31T8/6 | 32
FU1LL-R | FU31T8/6 | 27
FU1SE | FU40T12 | 43
FU1SS | FU40T12 | 43
FU2EE | FU40T12/ES | 72
FU2EL | FU40T12/ES | 63
FU2ES | FU40T12/ES | 72
FU2ILL | FU31T8/6 | 59
FU2ILL/T4 | FU31T8/6 | 56
FU2ILL/T4-R | FU31T8/6 | 49
FU2ILL-H | FU31T8/6 | 65
FU2ILL-R | FU31T8/6 | 52
FU2ILU | FU32T8/6 | 55
FU2ILU-R | FU32T8/6 | 48
FU2LL | FU31T8/6 | 60
FU2LL/T2 | FU31T8/6 | 59
FU2LL-R | FU31T8/6 | 54
FU2SE | FU40T12 | 72
FU2SL | FU40T12 | 63
FU2SS | FU40T12 | 72
FU3EE | FU40T12/ES | 115
FU3ILL | FU31T8/6 | 89
FU3ILL-R | FU31T8/6 | 78
FU3ILU | FU32T8/6 | 81
FU3ILU-R | FU32T8/6 | 73
FU3SE | FU40T12 | 115
H
H100/1 | H100 | 100
H150/1 | H150 | 150
H250/1 | H250 | 250
H300/1 | H300 | 300
H35/1 | H35 | 35
H42/1 | H42 | 42
H45/1 | H45 | 45
H50/1 | H50 | 50
H500/1 | H500 | 500
H52/1 | H52 | 52
H55/1 | H55 | 55
H60/1 | H60 | 60
H72/1 | H72 | 72
H75/1 | H75 | 75
H90/1 | H90 | 90
HLV50/1 | H50/LV | 60
HPS
HPS100/1 | HPS100 | 138
HPS1000/1 | HPS1000 | 1100
HPS150/1 | HPS150 | 188
HPS200/1 | HPS200 | 250
HPS250/1 | HPS250 | 295
HPS310/1 | HPS310 | 365
HPS35/1 | HPS35 | 46
HPS360/1 | HPS360 | 414
HPS400/1 | HPS400 | 465
HPS50/1 | HPS50 | 66
HPS70/1 | HPS70 | 95
I
I100/1 | I100 | 100
I1000/1 | I1000 | 1000
I100E/1 | I100/ES | 90
I100EL/1 | I100/ES/LL | 90
I110/1 | I110 | 110
I116/1 | I116 | 116
I120/1 | I120 | 120
I120/1 | I120 | 120
I125/1 | I125 | 125
I130/1 | I130 | 130
I135/1 | I135 | 135
I15/1 | I15 | 15
I150/1 | I150 | 150
I1500/1 | I1500 | 1500
I150E/1 | I150/ES | 135
I150EL/1 | I150/ES/LL | 135
I160/1 | I160 | 160
I170/1 | I170 | 170
I20/1 | I20 | 20
I200/1 | I200 | 200
I2000/1 | I2000 | 2000
I200L/1 | I200/LL | 200
I25/1 | I25 | 25
I250/1 | I250 | 250
I30/1 | I30 | 30
I300/1 | I300 | 300
I34/1 | I34 | 34
I36/1 | I36 | 36
I40/1 | I40 | 40
I400/1 | I400 | 400
I40E/1 | I40/ES | 34
I40EL/1 | I40/ES/LL | 34
I42/1 | I42 | 42
I448/1 | I448 | 448
I45/1 | I45 | 45
I50/1 | I50 | 50
I500/1 | I500 | 500
I52/1 | I52 | 52
I54/1 | I54 | 54
I55/1 | I55 | 55
I60/1 | I60 | 60
I60E/1 | I60/ES | 52
I60EL/1 | I60/ES/LL | 52
I65/1 | I65 | 65
I65/1 | I65 | 65
I67/1 | I67 | 67
I69/1 | I69 | 69
I7.5/1 | I7.5 | 8
I72/1 | I72 | 72
I75/1 | I75 | 75
I750/1 | I750 | 750
I75E/1 | I75/ES | 67
I75EL/1 | I75/ES/LL | 67
I80/1 | I80 | 80
I85/1 | I85 | 85
I90/1 | I90 | 90
I93/1 | I93 | 93
I95/1 | I95 | 95
LED
LED12GA | LED 12" Green Arrow | 8
LED12GB | LED 12" Green Ball | 12
LED12RA | LED 12" Red Arrow | 7
LED12RB | LED 12" Red Ball | 10
LED12YA | LED 12" Yellow Arrow | 9
LED12YB | LED 12" Yellow Ball | 17
LED8GB | LED 8" Green Ball | 8
LED8RB | LED 8" Red Ball | 6
LED8YB | LED 8" Yellow Ball | 12
LEDPCOUNT | Countdown Led | 7
LEDPH12OF | Overlay Filled Hand | 8
LEDPH12OO | Overlay Outline Hand | 6
LEDPH12F | Filled Hand Only | 7
LEDPH12O | Outline Hand Only | 6
LEDPH12SF | Side by Side Filled Hand | 7
LEDPH16OF | Overlay Filled Hand | 9
LEDPH16OO | Overlay Outline Hand | 8
LEDPH16SF | Side by Side Filled Hand | 11
LEDPH16SO | Side by Side Outline Hand | 6
LEDPP12OF | Overlay Filled Person | 7
LEDPP12OO | Overlay Outline Person | 6
LEDPP12F | Filled Person Only | 7
LEDPP12O | Outline Person Only | 5
LEDPP12SO | Side by Side Outline Person | 4
LEDPP16OF | Overlay Filled Person | 8
LEDPP16OO | Overlay Outline Person | 8
LEDPP16SF | Side by Side Filled Person | 8
LEDPP16SO | Side by Side Outline Person | 7
LEDO
LEDO37C | 5mm LED W | 37
LEDO50C | 5mm LED W | 50
LEDO37WP | 5mm LED W | 37
LEDO50WP | 5mm LED W | 50
MH
MH100/1 | MH100 | 127
MH100/1-L | MH100 | 111
MH1000/1 | MH1000 | 1077
MH125/1 | MH125 | 150
MH150/1 | MH150 | 184
MH150/1-L | MH150 | 167
MH1500/1 | MH1500 | 1608
MH175/1 | MH175 | 209
MH175/1-L | MH175 | 191
MH200/1 | MH200 | 232
MH200/1-L | MH200 | 219
MH250/1 | MH250 | 291
MH32/1 | MH32 | 42
MH320/1 | MH320 | 367
MH350/1 | MH350 | 395
MH360/1 | MH360 | 418
MH39/1 | MH39 | 56
MH39/1-L | MH39 | 44
MH400/1 | MH400 | 456
MH450/1 | MH450 | 507
MH50/1 | MH50 | 67
MH50/1-L | MH50 | 57
MH70/1 | MH70 | 94
MH70/1-L | MH70 | 79
MH750/1 | MH750 | 814
MV
MV100/1 | MV100 | 125
MV1000/1 | MV1000 | 1075
MV160/1 | MV160-SB | 160
MV175/1 | MV175 | 205
MV250/1 | MV250 | 290
MV40/1 | MV40 | 50
MV400/1 | MV400 | 455
MV50/1 | MV50 | 74
MV700/1 | MV700 | 780
MV75/1 | MV75 | 93
NEON
NEONEPH | Neon | 26
NEONEPP | Neon | 26
NEONMPDW | Neon | 81
NEONMPH | Neon | 45
NEONMPP | Neon | 38
REMOVED
Removed | None | 0